# ST TYDFIL’S COURT – EXTERNAL WALL REMEDIATION

# SPECIFICATION OF REQUIREMENTS

### 1. PROJECT OVERVIEW

St Tydfil’s Court, 12-storey residential block containing 66 flats.

Presence of:

- Chameleon Rockpanel rainscreen cladding (non-combustible A2) with no cavity barriers installed anywhere.

- 110 mm mineral wool insulation (A1 rated).

- ACM/EPS combustible spandrel panels running vertically the full height of the building (24 total).

- Sheared rivets, incorrect fixing points and missing sliding points on rainscreen panels.

- The PAS 9980 FRAEW classifies the risk as Medium/Tolerable, but mandates the installation of cavity barriers and the consideration of full spandrel replacement due to combustibility.

### 2. SCOPE OF WORKS (MANDATORY)

### 2.1 Access & Scaffold

Contractor must:

- Provide full-elevation scaffold to both rainscreen elevations.

- Include scaffold design by a competent temporary works engineer.

- Ensure load and tie-point compatibility with the building.

- Provide protective fans, debris netting, and exclusion zones

### 2.2 Removal & Reinstallation of Rainscreen Cladding

Contractor must remove, store, protect and reinstate all Rockpanel rainscreen panels necessary to gain access.

Requirements:

- Panels measure 1200mm (W) x 3050mm (H).

- Total working area confirmed as roughly 208 sqm

- Scope includes:

- Removal of all required fixings (including failed rivets).

- Labelling and indexing of panels for reinstatement.

- Safe storage of panels on-site (weatherproof).

- Reinstallation in accordance with Rockpanel manufacturer standards, ensuring correct use of sliding points (SP) and fixed points (FP).

- Replacement of sheared rivets and defective fixings.

### 2.3 Removal of Existing Insulation

Contractor must:

- Remove the existing 110mm A1 rockwool insulation to expose the substrate for fire barrier installation.

- Store insulation that is undamaged.

- Dispose of compromised insulation.

- Insulation must be removed to install barriers.

### 2.4 Supply & Installation of Cavity Barriers

This is the critical life-safety element and must be priced consistently.

Findings mandate:

- Horizontal cavity barriers (top, bottom, and each floor slab)

- 44lm per elevation × 2 elevations = 88lm total
 Vertical cavity barriers

- 60lm per elevation × 2 elevations = 120lm total

Requirements:

- Supply A1-rated ventilated/non-ventilated cavity barriers appropriate for the cavity dimensions (40mm cavity confirmed in intrusive report)

- Provide brackets, fixings, and intumescent materials.

- Install in full compliance with:

- PAS 9980 recommendations

- BS 8414 where relevant

- Manufacturer installation guidance

- Ensure continuous barriers with no gaps or discontinuities.

- Record installation locations with photographic evidence and as-built drawings.

### 2.5 Full Replacement of 24 Spandrel Panels – A1 Rated

Bidders must include:

- Removal of all existing 24 ACM/EPS spandrel infill panels.

- Supply of new A1-rated fire-resistant insulated spandrel panels sized to existing openings (400mm H × 1000mm W)

- Removal and reinstatement of glazing bars and gaskets.

- Full perimeter firestopping around spandrels.

### 2.6 Making Good & Reinstatement

Contractor must:

- Reinstall insulation (new or salvaged).

- Reinstall all rainscreen cladding panels.

- Replace any damaged trims, flashings, membranes or tapes.

- Seal all penetrations and ensure system continuity.

- Return elevations to pre-works cosmetic standard.

### 2.7 Quality Assurance & Certification

- At minimum, contractors must provide:

- Cavity barrier product certification

- Spandrel panel certification (A1 classification to EN 13501-1)

- Installation compliance sign-off

- Photographic evidence log (before, during, after)

- As-built drawings (PDF + DWG) showing all barrier locations

- Warranty documentation

- O&M manual

- Full certification before handover.

### 2.8 Health & Safety and Resident Protection

Contractor must:

- Provide RAMS aligned to fire protection best practice.

- Provide a resident engagement plan.

- Maintain fire escape routes at all times.

- Comply with Working at Height, hot works, and waste regulations.

### 2.9 Waste Management

Explicit requirements:

- Removal of all waste from site daily (particularly EPS panels).

- Provision of skips.

- No combustible storage left onsite overnight (critical due to PAS 9980 findings)

### 3. MEASURED QUANTITIES FOR PRICING

These are fixed and must be priced exactly as stated:

| Item | Quantity |
| --- | --- |
| Horizontal Cavity Barriers | 88 lm |
| Vertical Cavity Barriers | 120 lm |
| Rainscreen panel removal/reinstall | 208 sqm |
| Spandrel panels | 24 units (400 × 1000 mm) |
| Rockwool insulation depth | 110 mm |
| Cavity width | 40 mm |

### 4.1 Preliminaries

- Scaffold design & erection

- Welfare

- Traffic management

- Resident liaison

### 4.2 Rainscreen Works

- Removal of panels (208 sqm)

- Reinstallation

- Replacement fixings

### 4.3 Insulation Works

- Removal of existing insulation

- Disposal

- New insulation (sq m rate)

- Reinstallation

### 4.4 Cavity Barrier Installation

- Horizontal barriers (rate per lm × 88lm)

- Vertical barriers (rate per lm × 120lm)

- Brackets, fixings, firestopping

### 4.5 Spandrel Panel Replacement

- Removal of 24 existing panels

- Supply & install 24 A1 panels

- Removal/reinstall glazing bars & gaskets

### 4.6 Making Good

- Sealing, trims, membranes

- Any reinstatements

### 5. CONTRACTOR COMPETENCY REQUIREMENTS

Bidders must hold:

- Third-party accreditation (e.g., BM TRADA, IFC, FIRAS) for cavity barrier installation.

- Proof of training for rainscreen cladding systems.

- Demonstrated experience working on high-rise (>18m) building envelope remediation.