## Summary
Element | Sub-Element | Items | A | B | C | D | A | B | C | D | Condition
Roofs |  | 1 | 0 | 1 | 0 | 0 | 0 | 3.9 | 0 | 0 | 3.9 | 3.9 | B
| Flat Roofs | 1 | 0 | 1 | 0 | 0 | 0 | 3.9 | 0 | 0 | 3.9 | 3.9 | B
Electrical Services |  | 54 | 7 | 26 | 0 | 21 | 13.3 | 98.8 | 0 | 159.6 | 271.7 | 5.0315 | C
| Lighting - Fittings | 28 | 7 | 21 | 0 | 0 | 13.3 | 79.8 | 0 | 0 | 93.1 | 3.325 | B
| Power - Fittings | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 76 | 76 | 7.6 | D
| Power | 15 | 0 | 4 | 0 | 11 | 0 | 15.2 | 0 | 83.6 | 98.8 | 6.5867 | D
| Fire Alarms | 1 | 0 | 1 | 0 | 0 | 0 | 3.8 | 0 | 0 | 3.8 | 3.8 | B
| Lighting - Wiring | 1 | 0 | 1 | 0 | 0 | 0 | 3.8 | 0 | 0 | 3.8 | 3.8 | B
| Power - Wiring | 1 | 0 | 1 | 0 | 0 | 0 | 3.8 | 0 | 0 | 3.8 | 3.8 | B
Mechanical Services |  | 28 | 2 | 11 | 1 | 14 | 3.8 | 41.8 | 5.7 | 106.4 | 157.7 | 5.6321 | C
| Gas Distribution | 1 | 0 | 1 | 0 | 0 | 0 | 3.8 | 0 | 0 | 3.8 | 3.8 | B
| Hot and Cold Water Storage Tanks and Equipment | 5 | 2 | 1 | 1 | 1 | 3.8 | 3.8 | 5.7 | 7.6 | 20.9 | 4.18 | C
| Heating - Controls | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.6 | 7.6 | 7.6 | D
| Heat Source and Equipment | 11 | 0 | 5 | 0 | 6 | 0 | 19 | 0 | 45.6 | 64.6 | 5.8727 | D
| Heating - Distribution | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 22.8 | 22.8 | 7.6 | D
| Air Conditioning | 3 | 0 | 3 | 0 | 0 | 0 | 11.4 | 0 | 0 | 11.4 | 3.8 | B
| Ventilation | 4 | 0 | 1 | 0 | 3 | 0 | 3.8 | 0 | 22.8 | 26.6 | 6.65 | D
| Hot and Cold Water Storage Tanks and Equipment - Distribution | 1 | 0 | 1 | 0 | 0 | 0 | 3.8 | 0 | 0 | 3.8 | 3.8 | B
External Walls, Windows and Doors |  | 5 | 0 | 5 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 2.8 | B
| Windows and Doors | 3 | 0 | 3 | 0 | 0 | 0 | 8.4 | 0 | 0 | 8.4 | 2.8 | B
| Walls | 2 | 0 | 2 | 0 | 0 | 0 | 5.6 | 0 | 0 | 5.6 | 2.8 | B
Internal Walls and Doors |  | 8 | 0 | 8 | 0 | 0 | 0 | 19.2 | 0 | 0 | 19.2 | 2.4 | B
| Walls and Partitions | 3 | 0 | 3 | 0 | 0 | 0 | 7.2 | 0 | 0 | 7.2 | 2.4 | B
| Doors and Glazed Screens | 5 | 0 | 5 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 2.4 | B
Floors and Stairs |  | 14 | 0 | 14 | 0 | 0 | 0 | 8.4 | 0 | 0 | 8.4 | 0.6 | A
Redecorations |  | 1 | 0 | 1 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0.4 | 0.4 | A
Ceilings |  | 6 | 0 | 5 | 0 | 1 | 0 | 1 | 0 | 0.4 | 1.4 | 0.23333 | A
External Areas |  | 4 | 0 | 4 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0.8 | 0.2 | A
| Paths and Pedestrian | 1 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0.2 | 0.2 | A
| Soft Landscaping | 1 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0.2 | 0.2 | A
| Overall | [10 empty] | 21.197 | B

## Survey Report
Block_Name | Floor Level | Location_Name | Asset Unique ID | Date | Major Element (M or E) | Sub Element | Asset_Group | Asset_Element | Asset_SubElement | Asset_Component | _Asset_Specification | SFG_Code | Manufacturer | ModelNo | SerielNo | Comments | ConditionGrade | PriorityGrade | Asset_Status | Installation Year | CurrentAge (yrs) | BCIS LifeExpectancy | Life Remaining (adjusted) | Quantity | Unit | Costs Required
Block A | 0 (Ground) | RAG23 - Library | ON_63682722254_93211 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 3 | Nr | 1089.8688
Block A | 0 (Ground) | RAG23J - Male Toilet | ON_63682722636_93212 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 2 | Nr | 276.6923
Block A | 0 (Ground) | RAG23J - Male Toilet | ON_63682722675_93213 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | World Dryer | A 48 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 5 | 1 | 1 | Nr | 222.6623
Block A | 0 (Ground) | RAG23H - Disabled Toilet | ON_63682722846_93214 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 1 | Nr | 138.3461
Block A | 0 (Ground) | RAG23H - Disabled Toilet | ON_63682722846_93215 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | World Dryer | A 48 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 5 | 1 | 1 | Nr | 222.6623
Block A | 0 (Ground) | RAG23H - Disabled Toilet | ON_63682722872_93216 | 2019-01-10 | Mechanical Services | Ventilation | 5 - Services | 5.7 - Ventilation Systems | 5.7.2 - Local and Special Ventilation | Domestic Toilet Extract Fan c/w ancillaries - Wall Mounted | Domestic Toilet Extract Fan c/w ancillaries - Wall Mounted | 20-12 | Vent Axia | Solo | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 15 | 1 | 1 | Nr | 113.6054
Block A | 0 (Ground) | RAG23I - Female Toilet | ON_63682722977_93217 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 2 | Nr | 276.6923
Block A | 0 (Ground) | RAG23I - Female Toilet | ON_63682722977_93218 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | World Dryer | A 48 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 5 | 1 | 1 | Nr | 222.6623
Block A | 0 (Ground) | RAG23I - Female Toilet | ON_63682722977_93219 | 2019-01-10 | Mechanical Services | Ventilation | 5 - Services | 5.7 - Ventilation Systems | 5.7.2 - Local and Special Ventilation | Domestic Toilet Extract Fan c/w ancillaries - Wall Mounted | Domestic Toilet Extract Fan c/w ancillaries - Wall Mounted | 20-12 | Vent Axia | Solo | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 15 | 1 | 1 | Nr | 113.6054
Block A | 0 (Ground) | RAG23I - Female Toilet | ON_63682723019_93220 | 2019-01-10 | Mechanical Services | Hot and Cold Water Storage Tanks and Equipment | 5 - Services | 5.4 - Water Installations | 5.4.4 - Local Hot Water Distribution | Local Electric Hot Water Heaters | Unvented c/w valves/thermostat, 30 litre, 3kW | 32-10 | Santon | Electronics | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 15 | 1 | 1 | Nr | 686.4651
Block A | 0 (Ground) | RAG21 - Stores | ON_63682723304_93221 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 1 | Nr | 138.3461
Block A | 0 (Ground) | RAG21 - Stores | ON_63682723330_93222 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | MCB Distribution Board, TP&N, 12way inc MCBs | 44-07 | Square D | Load Centre | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 1970.475
Block A | 0 (Ground) | RAG21 - Stores | ON_63682723438_93223 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - SP&N | MCB Distribution Board, SP&N, 6 way inc MCBs | 44-07 | Dorman Smith | Loadlimiter | Unknown |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 356.5382
Block A | 0 (Ground) | RAG19 - Stores | ON_63682723742_93224 | 2019-01-10 | Mechanical Services | Air Conditioning | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.6 - Local Heating and Cooling | DX Unit - Ceiling Mounted | Cooling 12.20 kW, Heating 14.60 kW - Without Condenser | 59-07 | Daikin | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 1 | Nr | 3078.9923
Block A | 0 (Ground) | RAG24 - Toilet | ON_63682724760_93225 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - SP&N | MCB Distribution Board, SP&N, 12 way inc MCBs | 44-07 | MEM | MEMSHIELD | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 508.1387
Block A | 0 (Ground) | RAG24 - Toilet | ON_63682724760_93226 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - SP&N | MCB Distribution Board, SP&N, 6 way inc MCBs | 44-07 | MEM | MEMSHIELD | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 311.2155
Block A | 0 (Ground) | Female Toilet | ON_63682725047_93227 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2014 | 5 | 15 | 10 | 1 | Nr | 152.4152
Block A | 0 (Ground) | Female Toilet | ON_63682725047_93228 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Armitage Venestra | WAD 5 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 0 (Ground) | Disabled Toilet | ON_63682725256_93229 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2014 | 5 | 15 | 10 | 1 | Nr | 152.4152
Block A | 0 (Ground) | Disabled Toilet | ON_63682725256_93230 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Vent Axia | WAD 5 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 0 (Ground) | RAG06 - Hairdressing Studio | ON_63682726103_93231 | 2019-01-10 | Mechanical Services | Air Conditioning | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.6 - Local Heating and Cooling | DX Unit - Ceiling Mounted | Cooling 12.20 kW, Heating 14.60 kW - Without Condenser | 59-07 | Daikin | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 1 | Nr | 3078.9923
Block A | 0 (Ground) | RAG06 - Hairdressing Studio | ON_63682726121_93232 | 2019-01-10 | Mechanical Services | Air Conditioning | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.6 - Local Heating and Cooling | DX Unit - Ceiling Mounted | Cooling 12.20 kW, Heating 14.60 kW - Without Condenser | 59-07 | Daikin | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 1 | Nr | 3078.9923
Block A | 0 (Ground) | RAG06 - Hairdressing Studio | ON_63682726141_93233 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Menvier | BLN | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 2 | Nr | 726.5792
Block A | 0 (Ground) | RAS01 - Reception | ON_63682727223_93234 | 2019-01-10 | Mechanical Services | Heating - Distribution | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.2 - Local Heating | Electric, Wall mounted panel heater | 2000W | 29-02 | Unknown | AC3000N | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2010 | 9 | 10 | 1 | 1 | Nr | 356.4871
Block A | 0 (Ground) | RAS01 - Reception | ON_63682727353_93235 | 2019-01-10 | Mechanical Services | Heating - Distribution | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.2 - Local Heating | Electric, Wall mounted panel heater | 2000W | 29-02 | Unknown | AC3000N | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2010 | 9 | 10 | 1 | 1 | Nr | 356.4871
Block A | 0 (Ground) | RAS01 - Reception | ON_63682727577_93237 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 4 | Nr | 1453.1584
Block A | 0 (Ground) | RGB07A - Disabled Toilet | ON_63682728201_93238 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Fluorescent - Modular Recessed (Internal) | EM 600 x 600 mm. 4 x 18W T8. Modular recessed linear fluorescent; high frequency control gear; low brightness louver. | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 20 | 15 | 1 | Nr | 236.4348
Block A | 0 (Ground) | RGB07A - Disabled Toilet | ON_63682728201_93239 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Armitage Venestra | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 0 (Ground) | RBG09 - Teaching | ON_63682728524_93240 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2014 | 5 | 15 | 10 | 1 | Nr | 152.4152
Block A | 0 (Ground) | RBG09 - Teaching | ON_63682728575_93241 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - SP&N | MCB Distribution Board, SP&N, 6 way inc MCBs | 44-07 | MEM | MEMSHIELD 2 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 311.2155
Block A | 0 (Ground) | RBG09 - Teaching | ON_63682728575_93242 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - SP&N | MCB Distribution Board, SP&N, 6 way inc MCBs | 44-07 | MEM | MEMSHIELD | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 311.2155
Block A | 0 (Ground) | RBG09 - Teaching | ON_63682728838_93243 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Thorn | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 1 | Nr | 363.2896
Block A | 0 (Ground) | RBG11 - Teaching | ON_63682729178_93244 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Thorn | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 1 | Nr | 363.2896
Block A | 0 (Ground) | RBG11 - Teaching | ON_63682729221_93245 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | HRC Distribution Board, TP&N, 32A Incomer - 4 way | 44-07 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Damaged or missing equipment/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 568.4179
Block A | 0 (Ground) | RBG11 - Teaching | ON_63682729298_93246 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | MCB Distribution Board, TP&N, 4way inc MCBs | 44-07 | Schneider | Acti 9 Isobar | Unknown |  | B | P2 | Operational | 2012 | 7 | 20 | 13 | 1 | Nr | 1616.2274
Block A | 0 (Ground) | RBG14 - Teaching | ON_63682729658_93247 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - SP&N | HRC Distribution Board, SP&N, 32A Incomer - 12 way | 44-07 | MEM | MEMSHIELD | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 680.1044
Block A | 0 (Ground) | RBG15 - Common Room | ON_63682730003_93248 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - LED - Modular Recessed (Internal) | 600 x 600 mm. Modular LED luminaire; recessed into ceiling; including driver, polycarbonate optical lenses/diffuser, heat sink and 4000 K colour temperature | 36-03 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2017 | 2 | 20 | 18 | 1 | Nr | 415.1578
Block A | 1 | RB103 - Male Toilet | ON_63682731645_93249 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Deta | 1008 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 1 | RB101 - Theatre Workshop | ON_63682732053_93250 | 2019-01-10 | Mechanical Services | Ventilation | 5 - Services | 5.7 - Ventilation Systems | 5.7.1 - Central Ventilation | Fans - Central System - Duct Mounted | 5.0m3/s @ 200Pa. In line fan with backward curved centrifugal impellor; including ancillaries, matching flanges, flexible connectors and clips; 415 V, 3phase, 50 Hz motor; | 20-03 | Vortice | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 15 | 1 | 3 | Nr | 23648.4714
Block A | 1 | RAS1 - Stairs | ON_63682732500_93251 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - LED - Modular Recessed (Internal) | 600 x 600 mm. Modular LED luminaire; recessed into ceiling; including driver, polycarbonate optical lenses/diffuser, heat sink and 4000 K colour temperature | 36-03 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2017 | 2 | 20 | 18 | 8 | Nr | 3321.2626
Block A | 1 | RAS1 - Stairs | ON_63682732536_93252 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Emergilite | PE2311 | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 3 | Nr | 1089.8688
Block A | 1 | RA104 - Kitchen | ON_63682732837_93253 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | HRC Distribution Board, TP&N, 100A Incomer - 8 way | 44-07 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 2865.3647
Block A | 1 | RA104 - Kitchen | ON_63682732932_93254 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | HRC Distribution Board, TP&N, 100A Incomer - 8 way | 44-07 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 2865.3647
Block A | 1 | RA112 - Office | ON_63682733725_93255 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Thorn | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 1 | Nr | 363.2896
Block A | 1 | RA114 - Office | ON_63682734134_93256 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Thorn | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 1 | Nr | 363.2896
Block A | 1 | RA115 - Kitchen | ON_63682734229_93257 | 2019-01-10 | Mechanical Services | Hot and Cold Water Storage Tanks and Equipment | 5 - Services | 5.4 - Water Installations | 5.4.4 - Local Hot Water Distribution | Local Electric Hot Water Heaters | Unvented c/w valves/thermostat, 10 litre, 2.2kW | 32-10 | Redring | 22716801 | 28 221320 |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 1 | Nr | 420.3715
Block A | 1 | RA117 - Store | ON_63682734483_93258 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | HRC Distribution Board, TP&N, 100A Incomer - 4 way | 44-07 | Crabtree | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 1768.9205
Block A | 1 | RA117 - Store | ON_63682734483_93259 | 2019-01-10 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | HRC Distribution Board, TP&N, 100A Incomer - 8 way | 44-07 | Crabtree | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 1 | Nr | 2865.3647
Block A | 1 | RA118 - Female Toilet | ON_63682735024_93260 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 1 | RA118 - Female Toilet | ON_63682735054_93261 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 1 | RA118 - Female Toilet | ON_63682735076_93262 | 2019-01-10 | Electrical Services | Power - Fittings | 5 - Services | 5.1 - Sanitary Installations | 5.1.2 - Sanitary Ancillaries | Sanitary Appliances | Hand Dryer | 18-03 | Newlec | NL9 | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 5 | 1 | 1 | Nr | 222.6623
Block A | 1 | RA1C1 - Corridor | ON_63682735452_93263 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2014 | 5 | 15 | 10 | 1 | Nr | 152.4152
Block A | 1 | RA1C1 - Corridor | ON_63682735469_93264 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 2 | Nr | 726.5792
Block A | 0 (Ground) | RAGC1 - Corridor | ON_63682736657_93265 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - 2D Circular - Surface Mounted (Internal) | EM 2D 2Pin. 28W | 37-01 | Unknown | Unknown | Unknown |  | A | P1 | Operational | 2014 | 5 | 15 | 10 | 1 | Nr | 152.4152
Block A | 0 (Ground) | RAGC1 - Corridor | ON_63682736657_93266 | 2019-01-10 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.2 - Emergency Lighting | Luminaires - Self-Contained | EXIT luminaire. Maintained. 8 Watt | 37-01 | SupaLux | EMW1EB8M3 | Unknown |  | B | P2 | Operational | 2014 | 5 | 25 | 20 | 1 | Nr | 363.2896
Block A | 0 (Ground) | Plantroom | ON_63682794313_93267 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.5 - Heat Source | 5.5.1 - Heat Source | Boilers - Gas/Oil - Atmospheric | (High/low)(Conventional Flue) 300-340 kW | 05-03 | Ecoflam | Ecomax NC 300 | ZN3155002 | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 14578.4351
Block A | 0 (Ground) | Plantroom | ON_63682794313_93268 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.5 - Heat Source | 5.5.1 - Heat Source | Boilers - Gas/Oil - Atmospheric | (High/low)(Conventional Flue) 300-340 kW | 05-03 | Ecoflam | Ecomax NC 300 | ZN3155002 | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 14578.4351
Block A | 0 (Ground) | Plantroom | ON_63682794313_93269 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.5 - Heat Source | 5.5.1 - Heat Source | Boilers - Gas/Oil - Atmospheric | (High/low)(Conventional Flue) 300-340 kW | 05-03 | Ecoflam | Ecomax NC 300 | ZN3155002 | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 14578.4351
Block A | 0 (Ground) | Plantroom | ON_63682794313_93270 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Pump - Twin Head, Pipeline Mounted Pump | 12.0 l/s at 42 kPa - 1.1 kW Motor | 45-02 | Grundfos | Unknown | Unknown |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 3416.2339
Block A | 0 (Ground) | Plantroom | ON_63682794313_93271 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Pump - Single Head, Pipeline Mounted Pump | 5.0 l/s at 30 kPa - 0.37 kW Motor | 45-02 | Grundfos | 40 60/2 F | 96401915 |  | B | P3 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 1812.5178
Block A | 0 (Ground) | Plantroom | ON_63682794313_93272 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Pump - Single Head, Pipeline Mounted Pump | 5.0 l/s at 30 kPa - 0.37 kW Motor | 45-02 | Grundfos | 40-60/2 F | 96401915 |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 1812.5178
Block A | 0 (Ground) | Plantroom | ON_63682794313_93273 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Pump - Single Head, Pipeline Mounted Pump | 5.0 l/s at 30 kPa - 0.37 kW Motor | 45-02 | Grundfos | 40-60/2 F | 96401915 |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 1812.5178
Block A | 0 (Ground) | Plantroom | ON_63682794313_93274 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Pressurisation unit | 2,400 litre (c/w expansion vessel) | 40-25 | Boss | Unknown | Unknown |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 3919.7081
Block A | 0 (Ground) | Plantroom | ON_63682794313_93275 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Expansion Vessel - Closed (with membrane) | 500 litre | 32-12 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 15 | 1 | 1 | Nr | 1231.88
Block A | 0 (Ground) | Plantroom | ON_63682795095_93276 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Expansion Vessel - Closed (with membrane) | 500 litre | 32-12 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 15 | 1 | 1 | Nr | 1231.88
Block A | 0 (Ground) | Plantroom | ON_63682795117_93277 | 2019-01-11 | Mechanical Services | Hot and Cold Water Storage Tanks and Equipment | 5 - Services | 5.4 - Water Installations | 5.4.3 - Hot Water Services | Storage Calorifier | 400 Litre - Copper | 32-07 | Ecocharger | ECH 63-370 CE | 173006248105002 |  | A | P1 | Operational | 2017 | 2 | 25 | 23 | 1 | Nr | 9422.224
Block A | 0 (Ground) | Plantroom | ON_63682795283_93278 | 2019-01-11 | Mechanical Services | Hot and Cold Water Storage Tanks and Equipment | 5 - Services | 5.4 - Water Installations | 5.4.3 - Hot Water Services | Expansion Vessel - Closed (with membrane) | 10 - 50 litre | 32-12 | Aquasystem | ARB24 | Z2779919 |  | A | P1 | Operational | 2017 | 2 | 15 | 13 | 1 | Nr | 2397.75
Block A | 0 (Ground) | Plantroom | ON_63682795372_93279 | 2019-01-11 | Mechanical Services | Heat Source and Equipment | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.1 - Central Heating | Pump - Single Head, Pipeline Mounted Pump | 5.0 l/s at 30 kPa - 0.37 kW Motor | 45-02 | Grundfos | UPS 40-50 FB 250 | 52021405 | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2000 | 19 | 20 | 1 | 1 | Nr | 1582.113
Block A | 0 (Ground) | Plantroom | ON_63682795449_93280 | 2019-01-11 | Mechanical Services | Heating - Controls | 5 - Services | 5.12 - Communications, Security and Control Systems | 5.12.3 - Central Control / Building Management Systems | HVAC - Controls | Plant Controller, 96 I/O Points | 14-23 | BBM Control Systems | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 2005 | 14 | 15 | 1 | 1 | Nr | 4049.7937
Block A | 0 (Ground) | Plantroom | ON_63682795540_93281 | 2019-01-11 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | LV Distribution Boards - TP&N | MCB Distribution Board, TP&N, 6way inc MCBs | 44-07 | CPN | Unknown | Unknown |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 1602.7798
Block A | 0 (Ground) | Plantroom | ON_63682795590_93282 | 2019-01-11 | Mechanical Services | Gas Distribution | 5 - Services | 5.9 - Fuel Installations | 5.9.2 - Fuel Distribution Systems | Gas - Valves | Solenoid Valve/Shut Off | 40-22 | Elektrogas | VMR82-DN80 | Unknown |  | B | P2 | Operational | 2005 | 14 | 20 | 6 | 1 | Nr | 672.6
Block A | 0 (Ground) | Plantroom | ON_63682795656_93283 | 2019-01-11 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - Fluorescent - Surface Linear (Internal) | Twin lamp: Diffuser. 1800 mm 70W | 36-03 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 20 | 15 | 6 | Nr | 788.6942
Block A | All Block | All Block | ON_63682796045_93284 | 2019-01-11 | Mechanical Services | Heating - Distribution | 5 - Services | 5.6 - Space Heating & Air Conditioning | 5.6.2 - Local Heating | Double panel radiators with one convector surface, 750 mm high: | 900 mm long | 28-08 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | D | P3 | Operational | 1995 | 24 | 20 | 1 | 142 | Nr | 17781.5273
Block A | All Block | All Block | ON_63682796109_93285 | 2019-01-11 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - Fluorescent - Modular Recessed (Internal) | 600 x 600 mm. 3 x 18W T8. Modular recessed linear fluorescent; high frequency control gear; low brightness louver. | 36-03 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 20 | 15 | 430 | Nr | 54013.4932
Block A | All Block | All Block | ON_63682796210_93286 | 2019-01-11 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - Fluorescent - Surface Linear (Internal) | Twin lamp: Diffuser. 1800 mm 70W | 36-03 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 20 | 15 | 156 | Nr | 20506.0479
Block A | All Block | All Block | ON_63682796245_93287 | 2019-01-11 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - Low Voltage - Down lighters (Internal) | 118 mm dia. × 50 watt. Down lighter, recessed; low voltage; mirror reflector with white/chrome bezel; dimmable transformer; for dichroic lamps | 36-03 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 20 | 15 | 25 | Nr | 1836.7513
Block A | All Block | All Block | ON_63682979073_93293 | 2019-01-13 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - 2D Circular - Surface Mounted (Internal) | 2D 2Pin. 28W | 36-03 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2010 | 9 | 15 | 6 | 43 | Nr | 4759.1076
Block A | All Block | All Block | ON_63682979123_93294 | 2019-01-13 | Electrical Services | Lighting - Fittings | 5 - Services | 5.8 - Electrical Installations | 5.8.3.1 - Lighting Installations - Luminaires | Luminaires - Fluorescent - Recessed Compact (Internal) | 2 x 26W. Ceiling recessed asymmetric compact fluorescent down lighter; high frequency control gear; TCD lamp in 200 mm dia. luminaire; | 36-03 | Unknown | Unknown | Unknown |  | B | P2 | Operational | 2014 | 5 | 20 | 15 | 30 | Nr | 10631.313
Block A | All Block | All Block | ON_63683490981_157957 | 2019-01-19 | Electrical Services | Power | 5 - Services | 5.8 - Electrical Installations | 5.8.2 - Power Installations | Wiring | Small Power Wiring - including associated wireways | 0 | unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | B | P3 | Operational | 1957 | 62 | 30 | 5 | 420.9 | m2 | 4731.4421
Block A | All Block | All Block | ON_63683491079_157958 | 2019-01-19 | Electrical Services | Fire Alarms | 5 - Services | 5.11 - Fire and Lightning Protection | 5.11.4 - Fire Detection and Alarms | Fire Alarm - Wiring | FP200 | 22-02 | unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | B | P3 | Operational | 1957 | 62 | 30 | 5 | 420.9 | m2 | 3061.5214
Block A | All Block | All Block | ON_63683491147_157959 | 2019-01-19 | Mechanical Services | Ventilation | 5 - Services | 5.7 - Ventilation Systems | 5.7.1 - Central Ventilation | Ductwork Distribution | Ductwork Distribution | 16-02 | unknown | Unknown | Unknown | Excessive wear and tear of asset/components, | B | P3 | Operational | 1957 | 62 | 40 | 10 | 841.8 | m2 | 62924.55
Block A | All Block | All Block | ON_63683491240_157960 | 2019-01-19 | Mechanical Services | Hot and Cold Water Storage Tanks and Equipment | 5 - Services | 5.4 - Water Installations | 5.4.2 - Cold Water Distribution | Distribution Pipework - Galvanised Steel | Distribution Pipework - Steel | 40-17 | unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, | C | P3 | Operational | 1957 | 62 | 45 | 2 | 841.8 | m2 | 6895.7562
Block A | All Block | All Block | SMc_63683231567_99720 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Carpet tiles | B | P3 | Operational | 1957 | 62 | 20 | 5 | 2300 | Asset | 76705
Block A | All Block | All Block | SMc_63683231735_99721 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Carpet roll | B | P3 | Operational | 1957 | 62 | 20 | 5 | 55 | Asset | 1834.25
Block A | All Block | All Block | SMc_63683231900_99722 | 2019-01-16 | Ceilings | Ground Floor | Welsh Collage | Welsh Collage | Ceilings | Ground Floor | General | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Ceiling tiles exposed grid | B | P3 | Operational | 1957 | 62 | 30 | 5 | 75 | Asset | 3622.5
Block A | All Block | All Block | SMc_63683231989_99723 | 2019-01-16 | Ceilings | Ground Floor | Welsh Collage | Welsh Collage | Ceilings | Ground Floor | General | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Minor wear and tear of asset/components, Mineral fibre ceiling tiles exposed grid | B | P3 | Operational | 1957 | 62 | 30 | 5 | 1600 | Asset | 77280
Block A | All Block | All Block | SMc_63683232057_99724 | 2019-01-16 | Internal Walls and Doors | Doors and Glazed Screens | Welsh Collage | Welsh Collage | Internal Walls and Doors | Doors and Glazed Screens | Framing | 0 | Unknown | Unknown | Unknown | Timber frames | B | P3 | Operational | 1957 | 62 | 30 | 8 | 1 | Asset | 86.8
Block A | All Block | All Block | SMc_63683232098_99725 | 2019-01-16 | Internal Walls and Doors | Doors and Glazed Screens | Welsh Collage | Welsh Collage | Internal Walls and Doors | Doors and Glazed Screens | Framing | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Upvc framed internal windows | B | P3 | Operational | 1957 | 62 | 30 | 5 | 4 | Asset | 322
Block A | All Block | All Block | SMc_63683232177_99726 | 2019-01-16 | Internal Walls and Doors | Doors and Glazed Screens | Welsh Collage | Welsh Collage | Internal Walls and Doors | Doors and Glazed Screens | Other | 0 | Unknown | Unknown | Unknown | Fire doors with safety glass | B | P3 | Operational | 1957 | 62 | 20 | 10 | 100 | Asset | 97500
Block A | All Block | All Block | SMc_63683232452_99727 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Minor wear and tear of asset/components, Vinyl floor | B | P3 | Operational | 1957 | 62 | 20 | 10 | 8 | Asset | 301.6
Block A | All Block | All Block | SMc_63683232504_99728 | 2019-01-16 | Internal Walls and Doors | Walls and Partitions | Welsh Collage | Welsh Collage | Internal Walls and Doors | Walls and Partitions | Linings/Finishes | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Ceramic tiling | B | P3 | Operational | 1957 | 62 | 50 | 10 | 16 | Asset | 312
Block A | All Block | All Block | SMc_63683232568_99729 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Tiled floor | B | P3 | Operational | 1957 | 62 | 20 | 10 | 50 | Asset | 1885
Block A | All Block | All Block | SMc_63683232626_99730 | 2019-01-16 | Floors and Stairs | Staircases | Welsh Collage | Welsh Collage | Floors and Stairs | Staircases | Treads and Risers | 0 | Unknown | Unknown | Unknown | Carpeted treads and risers | B | P3 | Operational | 1957 | 62 | 20 | 8 | 1 | Asset | 35.96
Block A | All Block | All Block | SMc_63683232686_99731 | 2019-01-16 | Floors and Stairs | Staircases | Welsh Collage | Welsh Collage | Floors and Stairs | Staircases | Structure | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Steel framed with steel bannister | B | P3 | Operational | 1957 | 62 | 60 | 5 | 1 | Asset | 87.4
Block A | All Block | All Block | SMc_63683232740_99732 | 2019-01-16 | Floors and Stairs | Staircases | Welsh Collage | Welsh Collage | Floors and Stairs | Staircases | Soffit finish | 0 | Unknown | Unknown | Unknown |  | B | P3 | Operational | 1957 | 62 | 20 | 10 | 1 | Asset | 37.7
Block A | All Block | All Block | SMc_63683232940_99733 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Floor tiles - possible ACM | B | P3 | Operational | 1957 | 62 | 20 | 10 | 4 | Asset | 150.8
Block A | All Block | All Block | SMc_63683233561_99734 | 2019-01-16 | Ceilings | Ground Floor | Welsh Collage | Welsh Collage | Ceilings | Ground Floor | General | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Unknown material tiles | B | P3 | Operational | 1957 | 62 | 30 | 5 | 4 | Asset | 193.2
Block A | All Block | All Block | SMc_63683233718_99735 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Laminate wooden floors | B | P3 | Operational | 1957 | 62 | 20 | 10 | 330 | Asset | 12441
Block A | All Block | All Block | SMc_63683233813_99736 | 2019-01-16 | Floors and Stairs | Ground Floor | Welsh Collage | Welsh Collage | Floors and Stairs | Ground Floor | Screed and Finish | 0 | Unknown | Unknown | Unknown | Vinyl floor tiles | B | P3 | Operational | 1957 | 62 | 20 | 10 | 8 | Asset | 301.6
Block A | All Block | All Block | SMc_63683234113_99737 | 2019-01-16 | Ceilings | Ground Floor | Welsh Collage | Welsh Collage | Ceilings | Ground Floor | General | 0 | Unknown | Unknown | Unknown | Painted metal tile | B | P3 | Operational | 1957 | 62 | 30 | 8 | 350 | Asset | 18228
Block A | All Block | All Block | SMc_63683234504_99738 | 2019-01-16 | Internal Walls and Doors | Doors and Glazed Screens | Welsh Collage | Welsh Collage | Internal Walls and Doors | Doors and Glazed Screens | Ironmongery | 0 | Unknown | Unknown | Unknown | Plastic door handles | B | P3 | Operational | 1957 | 62 | 20 | 10 | 50 | Asset | 7150
Block A | All Block | All Block | SMc_63683234909_99740 | 2019-01-16 | Internal Walls and Doors | Doors and Glazed Screens | Welsh Collage | Welsh Collage | Internal Walls and Doors | Doors and Glazed Screens | Other | 0 | Unknown | Unknown | Unknown | Metal door | B | P3 | Operational | 1957 | 62 | 20 | 10 | 1 | Asset | 975
Block A | All Block | All Block | SMc_63683237902_99741 | 2019-01-16 | Floors and Stairs | Upper Floors | Welsh Collage | Welsh Collage | Floors and Stairs | Upper Floors | Screed and Finish | 0 | Unknown | Unknown | Unknown | Laminate wooden floor | B | P3 | Operational | 1957 | 62 | 20 | 10 | 300 | Asset | 11310
Block A | All Block | All Block | SMc_63683237952_99742 | 2019-01-16 | Ceilings | Upper Floors | Welsh Collage | Welsh Collage | Ceilings | Upper Floors | General | 0 | Unknown | Unknown | Unknown | Mineral fibre ceiling tiles exposed grid | B | P3 | Operational | 1957 | 62 | 30 | 10 | 1600 | Asset | 87360
Block A | All Block | All Block | SMc_63683238023_99743 | 2019-01-16 | Internal Walls and Doors | Walls and Partitions | Welsh Collage | Welsh Collage | Internal Walls and Doors | Walls and Partitions | Structure | 0 | Unknown | Unknown | Unknown | Solid blockwork wall | B | P3 | Operational | 1957 | 62 | 50 | 25 | 2800 | Asset | 249900
Block A | All Block | All Block | SMc_63683238089_99744 | 2019-01-16 | Redecorations | Internal | Welsh Collage | Welsh Collage | Redecorations | Internal | General | 0 | Unknown | Unknown | Unknown | Emulsion paint finish | B | P3 | Operational | 1957 | 62 | 5 | 10 | 2800 | Asset | 18200
Block A | All Block | All Block | SMc_63683238141_99745 | 2019-01-16 | Sanitary Services | Kitchens | Welsh Collage | Welsh Collage | Sanitary Services | Kitchens | Fittings | 0 | Unknown | Unknown | Unknown | Kitchen fittings | B | P3 | Operational | 1957 | 62 | 20 | 10 | 1 | Asset | 6500
Block A | All Block | All Block | SMc_63683238255_99746 | 2019-01-16 | Floors and Stairs | Staircases | Welsh Collage | Welsh Collage | Floors and Stairs | Staircases | Structure | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Blockwork construction | B | P3 | Operational | 1957 | 62 | 60 | 10 | 1 | Asset | 98.8
Block A | All Block | All Block | SMc_63683238320_99747 | 2019-01-16 | Floors and Stairs | Staircases | Welsh Collage | Welsh Collage | Floors and Stairs | Staircases | Treads and Risers | 0 | Unknown | Unknown | Unknown |  | B | P3 | Operational | 1957 | 62 | 20 | 10 | 1 | Asset | 37.7
Block A | All Block | All Block | SMc_63683238877_99749 | 2019-01-16 | Floors and Stairs | Upper Floors | Welsh Collage | Welsh Collage | Floors and Stairs | Upper Floors | Screed and Finish | 0 | Unknown | Unknown | Unknown | Vinyl tiled flooring | B | P3 | Operational | 1957 | 62 | 20 | 10 | 75 | Asset | 2827.5
Block A | All Block | All Block | SMc_63683239166_99751 | 2019-01-16 | Internal Walls and Doors | Walls and Partitions | Welsh Collage | Welsh Collage | Internal Walls and Doors | Walls and Partitions | Structure | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Partition wall | B | P3 | Operational | 1957 | 62 | 50 | 10 | 30 | Asset | 1989
Block A | All Block | All Block | SMc_63683239645_99752 | 2019-01-16 | Ceilings | Upper Floors | Welsh Collage | Welsh Collage | Ceilings | Upper Floors | General | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. Excessive wear and tear of asset/components, False ceiling partially missing | D | P2 | Operational | 1957 | 62 | 30 | 1 | 20 | Asset | 966
Block A | All Block | All Block | SMc_63683241431_99753 | 2019-01-16 | External Walls, Windows and Doors | Windows and doors | Welsh Collage | Welsh Collage | External Walls, Windows and Doors | Windows and doors | Framing | 0 | Unknown | Unknown | Unknown |  | B | P3 | Operational | 1957 | 62 | 30 | 25 | 800 | Asset | 98000
Block A | All Block | All Block | SMc_63683241482_99754 | 2019-01-16 | External Walls, Windows and Doors | Walls | Welsh Collage | Welsh Collage | External Walls, Windows and Doors | Walls | External Linings/Finishes | 0 | Unknown | Unknown | Unknown | Rendered wall finish | B | P3 | Operational | 1957 | 62 | 50 | 15 | 2400 | Asset | 87000
Block A | All Block | All Block | SMc_63683241522_99755 | 2019-01-16 | External Walls, Windows and Doors | Walls | Welsh Collage | Welsh Collage | External Walls, Windows and Doors | Walls | Structure | 0 | Unknown | Unknown | Unknown | External brickwork | B | P3 | Operational | 1957 | 62 | 60 | 25 | 500 | Asset | 137375
Block A | All Block | All Block | SMc_63683241561_99756 | 2019-01-16 | Roofs | Flat Roofs | Welsh Collage | Welsh Collage | Roofs | Flat Roofs | Other | 0 | Unknown | Unknown | Unknown | Flat roof system | B | P3 | Operational | 1957 | 62 | 20 | 25 | 3900 | Asset | 1706250
Block A | All Block | All Block | SMc_63683241611_99757 | 2019-01-16 | External Areas | Paths and Pedestrian | Welsh Collage | Welsh Collage | External Areas | Paths and Pedestrian | Paved Areas | 0 | Unknown | Unknown | Unknown |  | B | P3 | Operational | 1957 | 62 | 25 | 25 | 250 | Asset | 13125
Block A | All Block | All Block | SMc_63683241658_99758 | 2019-01-16 | External Walls, Windows and Doors | Windows and doors | Welsh Collage | Welsh Collage | External Walls, Windows and Doors | Windows and doors | Framing | 0 | Unknown | Unknown | Unknown | Curtain walling | B | P3 | Operational | 1957 | 62 | 30 | 20 | 12 | Asset | 1344
Block A | All Block | All Block | SMc_63683241709_99759 | 2019-01-16 | External Walls, Windows and Doors | Windows and doors | Welsh Collage | Welsh Collage | External Walls, Windows and Doors | Windows and doors | Other | 0 | Unknown | Unknown | Unknown | External doors - various | B | P3 | Operational | 1957 | 62 | 20 | 20 | 11 | Asset | 4400
Block A | All Block | All Block | SMc_63683241778_99760 | 2019-01-16 | External Areas | Soft Landscaping | Welsh Collage | Welsh Collage | External Areas | Soft Landscaping | General | 0 | Unknown | Unknown | Unknown |  | B | P3 | Operational | 1957 | 62 | 100 | 25 | 200 | Asset | 350
Block A | All Block | All Block | SMc_63683241900_99761 | 2019-01-16 | External Areas | Drainage | Welsh Collage | Welsh Collage | External Areas | Drainage | General | 0 | Unknown | Unknown | Unknown | Asset approaching end of life and lifecycle replacement/refurbishment should be considered. | B | P3 | Operational | 1957 | 62 | 60 | 10 | 550 | Asset | 85800
Block A | All Block | All Block | SMc_63683669461_99886 | 2019-01-21 | External Areas | Ancillary Premises | Welsh Collage | Welsh Collage | External Areas | Ancillary Premises | General | 0 | Unknown | Unknown | Unknown | Bike storage | B | P3 | Operational | 1957 | 62 | 0 | 10 | 1 | Asset | 5000
3150538.0017

## Methodology
|  |  | A | B | C | D
Element | %age | Factor | 1 | 2 | 3 | 4 | Percent
Roofs | 195% | 1.95 | 1.95 | 3.9 | 5.85 | 7.8 | 17.73%
Electrical Services | 190% | 1.9 | 1.9 | 3.8 | 5.7 | 7.6 | 17.27%
Mechanical Services | 190% | 1.9 | 1.9 | 3.8 | 5.7 | 7.6 | 17.27%
Sanitary Services | 180% | 1.8 | 1.8 | 3.6 | 5.4 | 7.2 | 16.36%
External Walls, Windows and Doors | 140% | 1.4 | 1.4 | 2.8 | 4.2 | 5.6 | 12.73%
Internal Walls and Doors | 120% | 1.2 | 1.2 | 2.4 | 3.6 | 4.8 | 10.91%
Floors and Stairs | 30% | 0.3 | 0.3 | 0.6 | 0.9 | 1.2 | 2.727%
Redecorations | 20% | 0.2 | 0.2 | 0.4 | 0.6 | 0.8 | 1.818%
Ceilings | 10% | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.9091%
External Areas | 10% | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.9091%
Fixed Furniture and Fittings | 10% | 0.1 | 0.1 | 0.2 | 0.3 | 0.4 | 0.9091%
Playing Fields | 5% | 0.05 | 0.05 | 0.1 | 0.15 | 0.2 | 0.4545%
|  |  | 11 | 22 | 33 | 44
Final Grade | High
A | 16.49
B | 21.5
C+ | 23.99
C | 25.99
C- | 30.99
D | 36