FIRE SAFETY SERVICING AND MAINTENANCE SERVICES 2026

VOLUME 3 - SPECIFICATION AND PRELIMINARIES

INDEX

- INTRODUCTION

- CONTRACT REQUIREMENTS

- REMEDIAL AND REPAIR WORKS

- PROGRAMME OF WORKS

- PROJECT METHOD STATEMENT

- STANDARDS AND REGULATIONS

- PROTECTION OF THE WORKS

- PRE-TENDER SURVEY

- ACCESS TO PROPERTIES

- PRACTICAL COMPLETION OF THE WORKS

- SAFETY STANDARDS AND REQUIREMENTS

- ENGINEERS AND OPERATIVES

- ADDRESSABLE SYSTEMS

- CONTRACT PAYMENTS

- SCHEDULE OF SERVICE TASKS

- KEY PERFORMANCE INDICATORS (KPI)

- CONTACTS & REPORTING

- WORKING FOR ADRA

- IT SECURITY REQUIREMENTS

- DESIRED DATA SYNCHRONISATION AND API INTEGRATION DEVELOPMENT

- INTRODUCTION

This agreement consists of testing, servicing and repairs of Fire Extinguishers, Emergency Lighting and Fire Alarm systems, Sprinkler systems, Lightning protection equipment, AOV’s and Dry risers in addition to firefighting equipment, and, where applicable, assuming responsibility for fire alarm monitoring services in each Adra (Tai) building as listed in Schedules of Property & Equipment in the Tender Documents.

The service area will cover the North and Mid Wales region, within the counties of Gwynedd, Conwy, Denbighshire, Flintshire and Wrexham, and any additional areas where Adra may have stock during the contract duration. Therefore, bidders will be expected to be able to provide full coverage across the whole of this area within the required testing schedules and emergency response times.

Bidders need to be aware that a reactive service is required. Bidders are advised to carefully consider the full details of the scope in detail, the rurality of some locations, and the ad-hoc nature of the emergency & remedial works.

THE SERVICES WE REQUIRE

As noted in Section 15 of this document, Adra will deliver testing, planned servicing, and maintenance of all fire safety equipment installed within our housing stock and office buildings across our full geographical area as defined within the Price Framework, ensuring that all units and systems operate efficiently, reliably, and in full compliance with manufacturer requirements, statutory obligations, and all applicable fire safety regulations.

- CONTRACT REQUIREMENTS

The scope of this contract covers the testing, servicing and maintenance of Fire Alarm Systems, Emergency Lighting, Automatic Fire Suppression Systems (AFSS - sprinklers / misting), Automatic Opening Ventilation Systems (AOV’s), Dry Risers, Portable Firefighting Equipment  and Lightning Protection Systems across Adra properties. This is outlined in the Pricing Schedule within the Tender Documents. The Service Provider shall allow for all such works and services within their Tender submission:

- Carrying out the servicing at each site as stipulated in the pricing document

- Undertake 2 visits annually to service the fire alarms as recommended by the relevant British Standards. Visits shall be carried out before the anniversary of the previous visit AND in the months shown in the Fire Alarm Schedule.

- Undertake weekly visits to test the fire alarm systems as recommended by the relevant British Standard.

- Undertake 1 visit annually to service the emergency lights as recommended by the relevant British Standards. Visits shall be carried out before the anniversary of the previous visit AND in the months shown in the Emergency lighting Schedule.

- Undertake monthly visits to test the emergency lighting systems as recommended by the relevant British Standards.

- Undertake 1 visit annually to service the Firefighting equipment as recommended by the relevant British Standards. Visits shall be carried out before the anniversary of the previous visit AND in the months shown in the Firefighting equipment Schedule.

- Undertake the repair and maintenance of the Fire alarm, emergency lighting systems and Firefighting equipment as per agreed SOR’s in the pricing document.

- Assuming the responsibility for, and the transferring of, the monitoring facilities of the fire alarm systems where applicable.

- In the first year of contract a full survey of the fire alarm, emergency lighting systems and Firefighting equipment at each site shall be carried out on the first service visit and any recommendations shall be made to the Compliance Officer if the installed systems do not comply with the current BS Recommendations. This shall be accompanied by a full and detailed listing of ALL devices/equipment on the systems indicating the types installed and the ‘fully identified’ rooms in which they are located. These listings shall also bear the make and model of the fire alarm panels. All of the preceding documents shall be delivered as described and a hard-copy left on site.

- Any changes found to the number, type and/or position of equipment/devices in any installation  on the following, and any subsequent, service visits shall be noted on the service sheets and the device/equipment listing amended accordingly. Updated listings shall be sent to the Compliance Officer with the service sheets.

- The Service provider shall include for the whole of the labour necessary to service and maintain all the existing equipment. The Service provider shall be required to undertake tests, adjustments and all minor work, e.g. adjust lamp, detector or screw connections, replacing fuses etc. as may be required to give an effective working installation.

- The Service provider shall provide any and all information regarding the systems they maintain to the Compliance Officer as and when it is required. This includes the full and comprehensive addressing labels of devices on addressable fire alarm systems. Information shall be provided within five working days.

- The Service provider shall provide a 24/7/365 fault repair service and attend any site required within 24 hours of a call request being made. A 2-hour site attendance response will be provided in the case of a total system failure or where alarms cannot be silenced.

- The Service provider shall provide legible service sheets/certificates for EACH service visit on EACH discipline for EACH site. These documents shall show:

- Name:

- Property Address:

- Date:

- Engineer’s name and signature:

- Results of the service:

- Devices/equipment tested:

- Defects found including any recommendations and/or information (sent weekly in Excel format):

- The service sheets shall be available to the Compliance Team, in ‘pdf’ format via the electronic client portal. All documentation must be accessible in real time or, where this is not possible, made available within one hour of the inspection if required for Quality Assurance purposes. The device listing sheets, when due, shall also be sent in this manner.

- Adra will require all service sheets/ job cards and invoices to be submitted via a dedicated portal as part of the contract with the successful service provider. Please see the tender documents for further information.

- The vast majority of sites have ‘Zone Charts’ attached near the fire alarm panel. In the first year of contract the Service provider shall check the accuracy of these charts and create new ones (for non-addressable systems) if necessary. Where no chart exists then the Service provider shall create one. Charts shall be A4 or A3 as appropriate to allow easy identification of each zone and be laminated and permanently attached to the wall within one metre of the fire alarm panel. All new or modified charts shall be in place by a date agreed with the client upon commencement of the contract with the successful service provider. Floor plans can be obtained by request from the Compliance officer.

- Each site shall have a current Log-Book available for inspection. If none exists, or needs replacing, then the service provider will provide one.

- Site Logbooks shall be completed on EVERY visit to site by the Service provider whether it be for servicing work, repairs or any other reason.

- The premises included in this contract are mainly in regular use and it is important that the continued day to day operations of services on these sites are not interfered with by the proposed works. It will therefore be necessary to ensure that all works are programmed via the site contacts so as not to cause disruption.

- Any serious faults found, that may prevent the systems from functioning normally, shall be brought to the attention of the Compliance Coordinator immediately for instructions on how to proceed. If the officer is not available then a call shall be made to the Compliance Manager on 0300 123 8084.

- Void calls  - The service provider shall undertake two documented visits, which is included within the terms of the pricing framework. If both attempted visits result in a void call, Adra will implement their “No Access” procedure. Any subsequent void call visits by the service provider may be charged in line with the agreed Price Framework. The service provider must provide geotagged, time stamped evidence of the two previous visit attempts (and any subsequent visits) in order to invoice for this charge.

- Communication requirements  - Where the service provider requires access to individual residence, the provider's responsibilities for resident liaison are as follows:

- The Service Provider is required to carry out the following communication as a minimum;

        - Notification of scheduled service with 21 days' notice (letter)

        - Notification of scheduled service with 7 days' notice (letter)

        - Notification of scheduled service with 24 hours' notice (telephone call or text message)

        - The above communications must be bilingual (Welsh & English)

- The Contract Manager will seek to assist the Provider to resolve any problems of access to individual properties with individual residents

- REMEDIAL AND REPAIR WORKS

All remedial and repair works, other than those included in the requirements within this document, shall only be carried out following an instruction and official order issued by Adra. Under no circumstances should any work be carried out without such an instruction. Whenever these works are carried out the Service provider should inform our Call Centre on 0300 1238084 or by E-mail on compliance@adra.co.uk when the work has been completed as soon as practicably possible. Invoices for these works should clearly show the hours worked, order number and charged at the rates provided in the pricing schedule and materials used, and shall be received and paid only if received electronically as agreed with Adra.

Remedial works valued up to £300 (inclusive of labour and materials) may be carried out without prior quotation, subject to appropriate documentation and reporting.

Remedial works exceeding £300 will be treated as major works and will require a formal quotation prior to authorisation of the Contract Manager.

The quotation and authorisation processes will be defined and agreed during the pre-contract meeting between the successful contractor and the Contract Manager.

- PROGRAMME OF WORKS

Servicing works at all sites shall be undertaken in the months stipulated in the ‘FA, EL and FFE Schedule’. The Service provider shall not deviate away from this schedule without the written consent of the Compliance Officer. The Service provider will be instructed, via a Formal Instruction, should a change be required to this schedule.

- PROJECT METHOD STATEMENT

Tenders shall be assessed on both a cost, competence and qualitative basis. For this purpose, the successful service provider shall submit a Project Method Statement post tender along with a programme of works.

As a minimum, the Project Method Statement shall include the following details:

a)	Management structure and methodology for the project.

b)	Project set-up procedures.

c)	The staff resources committed to each aspect of the project, their positions in the company and their relevant qualifications.

d)	Quality Assurance procedures.

e)	Method of arranging access to properties.

In addition to the items listed you may include in your Method Statement any additional information in support of your Tender e.g. references to specialist equipment used etc.

A technical description of carrying out the work on site is NOT required in the Project Method Statement.

- STANDARDS AND REGULATIONS

- The Service provider shall have full BAFE approval and maintain this for the duration of the contract.

- All materials, equipment and workmanship shall be in accordance with the specification.

- Where manufacturer’s instructions exceed the requirements of this document they shall be adhered to in their entirety.

- Unless otherwise specified all materials shall be new and these, together with equipment or work supplied or executed, shall comply with current Codes of Practice and with British Standards where applicable. Where particular Codes of Practice or British Standards are cited, such shall be deemed to refer to the current editions.

- Any instrument, rule or order made under any Act of Parliament or any regulations of any Local Authority or of any statutory undertaking which has any jurisdiction with regard to the Works or with whose systems the same are or will be connected, shall be complied with, and it will be ascertained that any necessary notices have been given to the Authority concerned.

- All electrical apparatus and work in connection therewith shall comply with the current edition of the IEE Regulations for Electrical Installations produced by the Institution of Engineering and Technology.

- All works and materials shall also comply with the requirements of the following: -

    - Local Authority Regulations, Recommendations, Requirements and Bylaws;

    - Water, Gas, Electricity, Fire Officer, British Telecom and all Public Authority and Statutory Regulations and Recommendations.

    - Health and Safety at Work Act, including all current regulations and statutory instructions issued by the Health and Safety Executive:

    - All relevant components of the British Standards BS5839 (fire alarms) and BS5266 (emergency lighting).

  - The following terms are used within this specification and shall be construed accordingly:

    - Service provider - person or persons appointed to carry out the Contract works and services;

    - Compliance Officer - person employing the Service provider to carry out the Contract works and services;

    - Engineer - person or persons appointed by the Service provider to represent him in connection with the servicing works described in this Specification.

- PROTECTION OF THE WORKS

- All fire alarm and emergency lighting equipment, other equipment in the vicinity of the plant being serviced, floor coverings and wall surfaces shall be protected during the undertaking of the works. Should there be any damage to the existing equipment or internal/external surfaces then the Service provider will be responsible for the complete repairs and/or re-decoration to the satisfaction of the Compliance Officer.

  - Adequate protection shall be provided against rough treatment, dust, grit, frost, etc.

- PRE-TENDER SURVEY

At the beginning of the contract and as part of the servicing and maintenance regime, the Service provider is required to undertake a full stock condition survey of the fire safety equipment and provide the following details to the client:

- Number of detectors, manual call points, panels, sounders and beacons

- Number of emergency lighting

- Number of fire extinguishers and blankets

- Number of sprinkler heads and pumps

- Age of the equipment and renewal dates

- Cost to renew

- Any additional equipment required

Furthermore, Adra recommends that prospective service providers familiarise themselves with the nature and geographical location of the stock, and equipment before submitting their final tender submission.

Any prospective service providers can request such a visit by submitting their request via the Question and Answer Facility attributed to the Contract Notice on Sell2Wales. Service providers should not attempt to access the site without prior arrangement.

- ACCESS TO PROPERTIES

- Access to all premises for the works and arrangement of appropriate times for the works to be carried out shall be made in advance, with the property’s Responsible Person, between the hours of 7.00 am and 7.00 pm (at a time agreed in advance by the client). In all cases it shall be the Service provider’s responsibility to liaise with the premises’ contact for access. When visiting sites, the Service providers/visitors logs shall be signed when entering and departing from site. The Service provider shall also complete and sign a ‘Consent to Work’ form which will be provided on site. However, the Service provider shall carry spares at all times should there be none available on site. If the Service provider cannot gain access to any property he/she shall contact the Compliance Officer for assistance as soon as possible.

- A comprehensive list of all the premises to be visited can found in the Tender documentation. No works shall be permitted to be undertaken outside of the hours above without the consent of the Compliance Officer.

- PRACTICAL COMPLETION OF THE WORKS

The date of Practical Completion of the Works shall be the 31st of March at the end of the relevant financial year, however in order to achieve Practical Completion, the following applies:

- All annual servicing work shall be completed by 28th February of each financial year of the contract;

- All copies of service certificates have been completed and accepted by the Compliance Officer before 28th March, at the latest, of the relevant financial year.

- All initial Device/Equipment Listing Sheets for all sites have been completed and accepted by the Compliance Officer, and copies left on site

- All Zone Charts are updated and/or provided and installed on site before

- NOTE – Work will NOT be paid for unless the relevant paperwork, noted in this document, has been submitted in a method agreed with Adra.

- SAFETY STANDARDS AND REQUIREMENTS

The Service Provider shall comply with all relevant health and safety legislation, including but not limited to statutory duties under the Health and Safety at Work etc. Act 1974, associated regulations, and applicable HSE guidance.

Service providers shall also observe:

  - Management of H&S at work Regulations Manual Handling Regulations

  - PUWER and LOLER Regulations

  - H.S.E. Documents HSG 210 & 213 Asbestos Essential Tasks Manual

The Service provider shall provide, and at their cost, all access and safety equipment required to undertake the works.

A copy of the successful Service provider’s Health and Safety Policy and Method Statements will be required for inspection before beginning any work.

All Service providers’ staff employed on the servicing works shall have undertaken ‘ASBESTOS AWARENESS TRAINING’ and certificates to verify this shall be available for inspection.

The Service provider shall not allow any person to carry out work on Adra’s plant or equipment to which they are not adequately and suitably qualified and trained for and/or experienced with.

Proof of the Service provider’s employees’ qualifications will need to be submitted on request.

The Service provider shall read and at all times adhere to any of Adra’s Health & Safety policies (copies will be issued to the successful tenderer).

In the event of any significant risks occurring, which are not covered in these documents, then separate Risk Assessments/Method Statements will be required from the Service provider prior to work commencing.

- ENGINEERS AND OPERATIVES

The service provider will ensure adequate arrangements are in place for vetting, appointing and monitoring the performance of subcontractors. It is the responsibility of the service provider to review & approve sub- contractors risk assessments & method statements, in line with contract requirements.

- ADDRESSABLE SYSTEMS

Service providers shall NOT tender prices for servicing, NOR carry out work on, addressable systems for which they and/or their Engineers do not have adequate and suitable training and expertise. This particularly relates to Gent, Protec, Siemens and Notifier systems. The Service provider shall also have access to all the necessary codes and passwords and be able to obtain any parts, manuals, technical information etc needed to carry out full and proper servicing of these systems as recommended by the manufacturers.

- CONTRACT PAYMENTS

Payments for the contracted servicing work will be made a maximum of once a month for any properties whose work has been completed (in one calendar month) and all relevant documents have been provided. The Service provider will present the Compliance Officer with a list of properties where payments are due as a ‘claim for payment’ and, once agreed, the payment will be made. A Claim Form will be provided on appointment. NO INVOICES are to be sent as part of this process except for the payment of VAT (for each claim) once the initial payment for the works have been made.

Payments for work carried out will not be made until all certificates and information sheets are completed to the satisfaction of, and returned by the due date to, the Compliance Officer and all Zone Charts and device/equipment listings have been completed and fitted / provided.

- SCHEDULE OF SERVICE TASKS

  - Fire Alarm System Maintenance Schedule

NOTE: All tests and servicing on equipment and trigger devices MUST be recorded in the Log-Book. Due to the variety and complexity of fire alarms and associated systems the following table only denotes the minimum maintenance to be carried out. The systems should be evaluated to determine whether the services of a specialist are required.

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing | Weekly | A manual call point should be operated during normal working hours. It should be confirmed that the control equipment is capable of processing a fire alarm signal and providing an output to fire alarm sounders, and to ensure that the fire alarm signal is correctly received at any alarm receiving centre to which fire alarm signals are transmitted. It is not necessary to confirm that all fire alarm sounder circuits operate correctly at the time of this test. The weekly test should be carried out at approximately the same time each week. | Certificates to be issues to the Compliance Officer |
| 2 Servicing | 6 months (twice a year) | Examine system Log-Book and take necessary any action. Test operation of alarm and indicating equipment for each zone. Ensure warning and information notices are displayed and legible. Ensure that spare call-point glasses are available on site. | Certificates to be issues to the Compliance Officer |
| 3 Control Panel | 6 months (twice a year) | Clean exterior of Control Panel. Ensure legends and labels are in place and legible. Clean and test lamps. Visually inspect interior for ingress of moisture and/or deterioration. Test ancillary functions including mains failure and fault alarm. |  |
| 4 System wiring | 6 months (twice a year) | Examine cables, containment and fixings. Examine flexible cables for wear, fraying braid and brittle insulation. Examine colour coding of cables and ensure cores are correctly connected. Examine for loose terminals/connections. |  |
| 5 Batteries | 6 months (twice a year) | Test batteries for EMF and specific gravity of electrolyte and top-up if necessary. Ensure battery terminals/connections are clean and tight. Clean and grease terminals as necessary. | Replace any faulty batteries. Old ones shall be disposed of in accordance with COSHH Regulations. |
| 6 Chargers | 6 months (twice a year) | Examine meters for condition and operation. Test outputs. |  |
| 7 Detectors | 6 months (twice a year) | Visually inspect for damage or other defects/adverse conditions, e.g. coated of paint, likely to interfere with the correct operation of the devices. | Replace any faulty detectors. |
| 8 Sounders | 6 months (twice a year) | Test operation of ALL sounders. Visually inspect for damage and/or deterioration. Ensure positioning/siting of device is still suitable. |  |
| 9 Auxiliary functions | 6 months (twice a year) | Test operation of door-release mechanisms. Test operation of autodial and other linked systems. Test electrical initiation system of fixed firefighting installations. |  |
| 10 General | Annually | As in action 2 and check complete installation at Main Control point. | Certificates to be issues to the Compliance Officer |
| 11 Control Panel | Annually | As action 3 and examine insulation of terminal wiring and ensure connections are sound. |  |
| 12 Manual Call Points | Annually | Visually inspect to ensure that they all remain conspicuous and unobstructed. Manually activate a point to ensure the system is active. Examine fixings and tighten if necessary. Examine insulation of terminal wiring and ensure connections are sound. |  |
| 13 Heat Detectors | Annually | As action 7 and: All detectors should be tested for correct operation by the application of a heat source. Examine fixings and tighten if necessary. Examine insulation of terminal wiring and ensure connections are sound. |  |
| 14 Smoke Detectors | Annually | As action 7 and: Clean all detectors. All detectors should be tested according to manufacturer’s recommendations for correct operation, sensitivity and stability. Examine fixings and tighten if necessary. Examine insulation of terminal wiring and ensure connections are sound. |  |
| 15 Sounders | Annually | As action 8 and: Examine fixings and tighten if necessary. Examine insulation of terminal wiring and ensure connections are sound. |  |
| 16 Auxiliary functions | Annually | As action 9 and: Examine fixings and tighten if necessary. Examine insulation of terminal wiring and ensure connections are sound. |  |

15.2 	Emergency Lighting Maintenance Schedule

NOTE: All tests and services on emergency lighting equipment and trigger devices MUST be recorded in the Log-Book. Due to the variety and complexity of various emergency lighting systems the following table only denotes the minimum maintenance to be carried out. The systems should be evaluated to determine whether the services of electrical specialists are required.

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing | Monthly | Carry out the following tests: a) Switch on, in emergency mode, each luminaire and each internally illuminated exit sign from its battery power by simulation of failure of the supply to the normal lighting for a period sufficient to ensure that each lamp is illuminated. During this period, all luminaires and signs shall be checked to ensure that they are present, clean and functioning correctly. At the end of this test period the supply to the normal lighting should be restored and any indicator lamp or device checked to ensure that it is showing that the normal supply has been restored. b) In addition to a) above, for central battery systems, the correct operation of system monitors shall be checked. c) In addition to a) above, for generating sets, refer to the requirements of ISO 8528-12. | Certificates to be issues to the Compliance Officer. |
| 2 Testing | Annually | In addition to the tests carried out in item-1 (above), carry out the following tests: - Each luminaire and internally illuminated sign shall be tested as per the monthly test but for its full rated duration in accordance with the manufacturer’s information. b) The supply to the normal lighting shall be restored and any indicator lamp or device checked to ensure that it is showing that the normal supply has been restored. The charging arrangements should also be checked for proper functioning. c) In addition, for generator sets, refer to the requirements of ISO 8528-12. | Certificates to be issues to the Compliance Officer. Ensure that these tests are carried out at such a time as to ensure that the re-charge time is allowed for when building has least occupancy. All tests shall be recorded in the site Log-Book. |
| 3 Battery | Annually | Check condition and date of expected life. | When batteries are replaced the old ones shall be disposed of in accordance with COSHH Regulations. |
| 4 Electrical Installation | Annually | Examine all flexible cables for wear, fraying braid and brittle insulation. Examine all connections. | Report any faults to the Compliance Officer. Certificates to be issues to the Compliance Officer |
| 5 Lighting programmers and sensors | Monthly | Check operation of programmers and sensors so they operate the lights. Make sure that programmers keep to the correct time. |  |
| 6 Lighting programmers | 6 Months (twice a year) | Adjust the programmer to allow the lighting to operate in line with seasonal changes |  |

15.3 	Firefighting Equipment Maintenance Schedule

Fire Extinguishers

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing and servicing | Annually | Fire extinguisher servicing should be carried out once a year to the standard laid down under BS 5306-3:2017 1.Visually inspect the fire extinguisher for corrosion and damage. 2.Check that the extinguisher has not been used, by checking the following: ◦Safety pin and tamper seal are in place ◦Pressure gauge reading (indicating needle should be in the green area. This is not applicable for CO2 fire extinguishers) 3.Check that the operating instructions on the extinguisher are clear and legible. 4.Remove the discharge hose and check for blockages and corrosion. ◦Once the discharge hose has been removed replace the ‘O’ ring. 5.Weigh the extinguisher and record on the service label. ◦If there is more than a 10% weight loss, investigate and recharge. 6.Wipe down the extinguisher. 7.Ensure that the wall mountings are secure and in good condition before replacing the appliance back on the wall. | Certificates to be issues to the Compliance Officer. All tests shall be recorded in the site Log-Book |

15.4	Fire Blankets

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing and servicing | Annually | Engineers will ensure that the firefighting equipment is serviced and maintained to I.S. 291:2015 & BSEN 1869:1997 and will: 1.Remove the fire blanket from its cover 2.Check the fire blanket and cover are in good condition 3.Replace the fire blanket in its cover and record details on a service label 4.Review the fire blanket siting and ensure that its location is not too close to a fire risk 5.Ensure the fire blanket is secured at the correct height and can be opened without obstruction | Certificates to be issues to the Compliance Officer. All tests shall be recorded in the site Log-Book |

15.5	Sprinkler & Misting Systems

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing and servicing | Annually | Undertake annual testing, servicing and maintenance of sprinkler and misting systems to the current BS 9251:2014. To be undertaken by a suitably experienced and competent sprinkler service provider. Check that the system has not been modified except in accordance with this British Standard. The system should be tested as follows. - The system should be visually inspected wherever possible for leaks. Should a leak be suspected the pipework should be pressure tested to 1.5times working pressure for 1h. - Both internal and external alarms should be left active so that their satisfactory operation can be audibly verified. - The sprinkler system should be flow tested for 1min at the drain and test valve or the highest test point of the installation pipework and ensure that the conditions of 5.2.5 are met. - Stop valves should be exercised to ensure free movement. - Where trace heating is installed check operation. - The person carrying out the inspection should complete and sign the Log Book | Certificates to be issues to the Compliance Officer. All tests shall be recorded in the site Log-Book. |
| - Sprinkler heads | Annually | Check the sprinklers' heat sensing capacity and their spray pattern is not impeded. |  |
| 3 Alarm | Annually | Check the alarm is effective and can be heard in all parts of the building. |  |
| 4 Drain and test valve | Annually | Check that the minimum flow rate recommended in this British Standard is achieved at the drain and test valve. |  |

15.6	Automatic Opening Vents (AOV)

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing | Weekly | The weekly AOV test forms part of the Fire Alarm weekly test. As the alarm is activated the AOV should release / open fully without obstruction. If any of the AOV smoke vents are found to be non-functioning during routine testing, or has become damaged, immediate action needs to be taken to remedy the faults and/or failures | All tests shall be recorded in the site Log-Book |
| 2 Testing and servicing | 6 Months (twice a year) | The 6 monthly AOV system servicing should include functional testing and preventative maintenance. All moving parts should be checked for wear and signs of failure and all applicable components should be lubricated as per manufacturers maintenance guidelines. All electrical connections should be checked for connectivity and signs of corrosion causing poor connectivity and possible shorting / earth leakage. If any of the AOV smoke vents are found to be non-functioning during routine testing, or has become damaged, immediate action needs to be taken to remedy the faults and/or failures | Certificates to be issues to the Compliance Officer. All tests shall be recorded in the site Log-Book |

15.7	Dry Risers Systems

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing and servicing | 6 Monthly & Annually | All maintenance activities should be in line with BS 9990:2015, which should include, but not be limited to: - Six-Monthly Visual Inspection: Cabinets: Check for damage, locks, hinges, glass, and clear signage. Valves: Inspect all landing valves, inlet valves, and drain valves for damage or theft. Lubrication: All moving parts should be lubricated. Immediate Action: Any defects found must be repaired immediately to avoid system failure. - Annual Wet Pressure Test: Procedure: The system is filled with water and pressurized, typically to 12 bar (175 psi) for at least 15 minutes to check for leaks. Dry Riser Inlet: The inlet breech must be checked, with washers and blank caps replaced if necessary. Drainage: The system must be fully drained after the test to prevent freezing and corrosion. Documentation: A certificate of conformity is issued, confirming the system is operational and meets regulations | Certificates to be issues to the Compliance Officer. All tests shall be recorded in the site Log-Book |

15.8	Lightning Protection Systems

| Item number | Frequency | Action | Notes |
| --- | --- | --- | --- |
| 1 Testing and servicing | Annually | All maintenance activities should be in line with BS EN 62305, which should include, but not be limited to: - Visual Inspection: Thoroughly examine all components for damage, corrosion, or degradation, including air terminals (rods), down conductors, and earthing systems. - Electrical Testing: Measure the resistance to earth of the system and individual electrodes to ensure effective conductivity. - Connection Checks: Verify that all joints, bonds, and clamps are secure and not corroded - Surge Protection: Inspect Surge Protection Devices (SPDs) for damage and ensure they are operational - Post-Modification Checks: Inspect the system immediately following any construction, repairs, or alterations to the building - Documentation: Maintain a comprehensive log of all inspections, test results, and remedial works performed, as this is essential for insurance and safety audits | Certificates to be issues to the Compliance Officer. All tests shall be recorded in the site Log-Book |

- KEY PERFORMANCE INDICATORS (KPI)

- Performance of the works and Services will be managed by adopting a suite of KPIs that will be relevant to each project. Broadly these KPIs will be based around, but not limited to:

    - Adra's (as client) satisfaction;

    - Tenant satisfaction;

    - HSQE (health, safety, quality and environment) objectives;

    - Programme and duration targets;

    - Commercial aspects;

    - Level of defects/issues/complaints; and

    - Community benefits (social value – in line with tender submission).

Adra has set out its expectations in terms of performance standards and has included this in the tender documentation. This will be used as the basis of measuring the performance of Adra’s contract with the service provider.

- CONTACTS & REPORTING

Contacts

Trwsio Call Centre:

Office Hours 8:00am – 6:00pm Monday to Friday

| Call centre Telephone: | 03001238084 |
| --- | --- |

Email: compliance@adra.co.uk & trwsio@adra.co.uk

For any ‘work specific’ queries please contact:

Peter Jones, Compliance Coordinator

Adra Tai Cyf

Ty Coch

Llys y Dderwen

Bangor

Gwynedd

LL57 4BL

Telephone: 0300 123 80 84

Email: compliance@adra.co.uk

Documents

SITE INSPECTION FORM – BEFORE WORK COMMENCES

| Site Location / Site ID: |  |
| --- | --- |
| Person Inspecting Site: |  |
| Any Service providers On Site: |  |
| Date Of Visit: |  |

Description Of Proposed Works

| Description Of Proposed Works |  |  |  |
| --- | --- | --- | --- |
| Observation | Good | Poor | Comment |
| Access |  |  |  |
| Security |  |  |  |
| Traffic |  |  |  |
| Parking |  |  |  |

| Environment |  |
| --- | --- |
| Observation | Comment |
| What is around the site? |  |
| What is the working environment? |  |
| Natural or Artificial Light |  |
| Trees over hanging the site. |  |
| Any Vermin? |  |
| Will weather affect work? |  |
| Other. |  |

| Existing Information on Site |  |
| --- | --- |
| Observation | Comment |
| Health & Safety Manual. |  |
| Waste Management Information |  |
| Traffic Management Information. |  |
| Emergency Procedure Information. |  |
| Existing Construction Phase Plan |  |
| Existing Risk Assessments / Method |  |
| Statements. |  |
| Existing COSHH Assessments |  |
| Existing Site Procedures |  |
| Existing Health and Safety File |  |
| Existing Maintenance Records. |  |

| Existing Welfare Facilities on Site |  |  |  |
| --- | --- | --- | --- |
| Observation | Yes | No | Comment |
| Toilet / Washing Facilities |  |  |  |
| Canteen |  |  |  |
| Drying Room |  |  |  |
| Water Supply |  |  |  |
| Power Supply |  |  |  |
| Other |  |  |  |

| Site |  |
| --- | --- |
| Observation | Comment |
| Will you need to notify the site owner before entering the site (If yes, full contact details) |  |
| Excavations |  |
| Demolition |  |
| Plant / Equipment On Site. |  |
| Scaffolding |  |
| Ladders / Steps |  |
| Lifting equipment |  |
| Noise Conditions |  |
| Tripping / Slipping Hazards. |  |
| Overhead Cables |  |
| Overhead height restrictions |  |
| Working at height. |  |
| Confined Space Issues |  |
| Waste Management |  |
| Access / Egress though the site. |  |
| Safety Zones / Restricted Areas |  |
| Other Activities / Works / Service providers |  |
| Other |  |
| Excavations |  |
| Demolition |  |

Overall View of the Site

Hot work permit

Trwydded Caniatau Gwaith Poeth

Hot Works Permit

Rhif Cyfeirnod

Ref Number:

Contractwr/Service provider: …………………………………………………..

Cyfeiriad Safle’r Gwaith/Site Address:

| AR GYFER GWAITH GYDA / FOR WORK WITH …………..………………….. |  |
| --- | --- |
| Safle penodol y gwaith: Exact location of work: |  |
| Disgrifiad o’r gwaith: Description of work to be done: |  |
| Deunyddiau llosgadwy wedi eu gorchuddio, glychu neu eu symud: Combustibles removed, covered or damped down: | Do/Yes ☐ N/A ☐ |
| Diffodwr tân gerllaw: Fire extinguisher to hand: | Oes /Yes ☐ Math / Type: N/A ☐ |
| Defnyddir chwistrellwr gwrth-dân: Fire retardant spray used: | Oes/Yes ☐ N/A ☐ |
| Defnyddir mat tân: Fire mat used: | Oes/Yes ☐ N/A ☐ |
| Oes angen ‘fire watch’ Is fire watch required | Oes/Yes ☐ Enw/Name: N/A ☐ |
| Rhagofalon arbennig pellach: Further special precautions: |  |
| Mae’r safle Gwaith hwn wedi ei archwilio, y rhagofalon angenrheidiol mewn lle a rhoddir chaniatad i’r Gwaith barhau. The location where this work is to be done has been examined, necessary precautions taken and permission is granted for this work. | ARWYDDWYD / SIGNED ………………………………………………………………. SAWL SY’N GYFRIFOL AM RHOI CANIATAD INDIVIDUAL RESPONSIBLE FOR AUTHORISING |
| Trwydded yn dechrau / Permit Start: / / Amser dechrau’r Gwaith / Time started:…………………. Trwydded yn do di ben / Permit Expires: / / Cwblhawyd y Gwaith / Completed: / / |  |
| GWIRIAD TERFYNOL (Watch Tân) Archwiliwyd y man gwaith a'r ardaloedd cyfagos lle gall gwres ledaenu (gan gynnwys lloriau uwchben ac o dan, ac ar yr ochr arall i’r waliau) 1 awr ar ôl i’r gwaith ei gwblhau, ac fe’u canfuwyd yn ddiogel. FINAL CHECK UP (Fire Watch) Work area and adjacent areas to which heat might have spread (including floors above and below, and on the opposite side of walls) were inspected 1 hr after operation was completed and were found firesafe. Arwyddwyd/Signed:…………………………………… Person Cymwys / Competent Person) |  |

- WORKING FOR ADRA

Service providers who are working for Adra are representing us. It is therefore important that they have read and understood some of our key policies relating to things like the Welsh language, Customer Service, Health and safety and safeguarding, and are willing to work to these.

These policies are included within this request for quotation pack, and bidders will be asked as part of the quality checks to confirm their acceptance of these policies.

If Adra is to be tagged, photographed, or mentioned in any social media posts, this must only occur on an official business page that is dedicated to professional use. Personal social media accounts must not be used for such purposes. The business page should represent the organisation professionally and must not include or reflect any personal political views or opinions. This ensures that all content aligns with Adra’s values and protects the integrity of our brand.

- IT SECURITY REQUIREMENTS

As the delivery of this contract will involve the collection and processing of sensitive customer information classified as Tier 1, the service provider must comply with the highest level of security and assurance controls. These requirements apply to the primary service provider (primary processor) and all sub-contractors delivering the service, including third-party data collection tools, hosted portals or any platform processing our data.

Compliance with the requirements outlined below is mandatory and constitutes a pre-condition for contract award and contract continuation.

19.1	 Security Standards & Accreditation

19.1.1	Both the primary processor and any sub-processor handling our data must meet our minimum-security standard (ITss10). Please see Volume 7 of this tender pack.

19.1.2	The entity processing or hosting our data should hold current ISO 27001 certification (with in-scope statement), SOC 2 Type II accreditation or Cyber Essentials Plus. A provider without these accreditations must provide evidence demonstrating robust information security management in the form of:

- Information Security Policy

- Acceptable Use Policy

- Access Control Policy

- Incident Response Procedure

- Data Retention & Disposal Policy

- Backup & Recovery Policy

- Hardware encryption details (i.e. how mobile devices are encrypted)

19.2	 Security Questionnaire

19.2.1	The primary processor must complete our Tier 1 security questionnaire prior to contract award and annually thereafter on each contract anniversary.

19.2.2	The primary processor must cascade relevant control requirements to their sub-processor.

19.2.3	Where appropriate expertise does not sit with the primary processor, the sub-processor must complete the relevant sections directly.

19.2.4	The successful service provider will be required to complete the following Vendor Security Questionnaire Forms prior to contract commencement:

- Web Application Security Questionnaire: Here﻿

- Infrastructure Questionnaire: Here﻿

- Privacy and Security: Here

19.3	 Penetration Testing Assurance

19.3.1	For any supplier providing software or a service platform used to process our data, Adra require a redacted executive summary of the most recent independent external penetration test. This must confirm:

- No unresolved High or Critical findings

- Defined remediation timelines for any medium findings

19.3.2	Penetration testing must be undertaken annually or following significant system changes.

19.4	 Flow-Down Obligations

19.4.1	The Primary Processor (Fire Safety service provider) must ensure that any Sub-Processor (e.g. portal provider) is contractually bound by written obligations that provide at least the same level of data protection, security controls, and audit rights as set out in any agreement.

19.5	 Sub-Processor Changes

19.5.1	Any proposed change or addition of a sub-processor during the term of the contract must:

- Be notified to us in writing in advance; and

- Be subject to the same due diligence and contractual controls as the original appointment.

- DESIRED DATA SYNCHRONISATION AND API INTEGRATION DEVELOPMENT

Although the following items are not mandatory requirements of the contract, Adra recognises the importance of achieving the highest possible standards of data accuracy, consistency, and integrity across its own and partner organisations internal systems. To support this, Adra considers API-based integration and automated data synchronisation to be key enablers for ensuring that data remains current, reliable and aligned with organisational processes.

Adra has therefore identified the following desired development opportunities which, while not essential for contract compliance, would be viewed as added value and would strengthen the overall service provision.

### System Integration and Data Synchronisation

Where the proposed solution processes, stores, or otherwise utilises the Organisation’s data (including but not limited to tenant, customer, employee, contractor, or compliance-related information), the Supplier should provide a system architecture that supports secure, standards-based API integration with the Organisation’s internal systems.

The Organisation’s preferred operating model is to maintain a single authoritative source of record within its internal systems. Third-party platforms must therefore be capable of:

- Bidirectional or controlled synchronisation of relevant data fields via documented APIs.

- Supporting near real-time or scheduled automated updates to ensure data consistency across systems.

- Enabling automated updates when data is amended within the Organisation’s internal systems (e.g., changes to contact details, tenancy status, vulnerability indicators, communication preferences).

- Preventing the creation of unmanaged data silos that result in duplicated, stale, or inconsistent records.

### Data Integrity and Regulatory Compliance

All data shared with service providers must be stored and processed within the UK or a GDPR approved location.

The supplier acknowledges that data inconsistency between systems may:

- Create operational inefficiencies

- Introduce data integrity risks

- Increase the likelihood of inaccurate communications

Create potential compliance exposure under applicable data protection legislation, including UK GDPR, particularly in respect of accuracy obligations (Article 5(1)(d)).