## Front Page
Revision | Description | Date | Author | Reviewer | Approver
1 | PM Draft Issue | 2025-08-22 | Sean Jardine | Mathew Preece | Mathew Preece
2 | PM Feedback | 2025-09-05 | Sean Jardine | Mathew Preece | Mathew Preece
Energy Efficiency and Decarbonisation Audit
Prepared by: Sean Jardine
For: University of Wales Trinity Saint David
Site: Dynefor
Date: 05/09/2025
Document Ref: 319232-DYN
Issue-2.00
Disclaimer
The Welsh Government Energy Service (“WGES”) is funded by the Welsh Government with the aim of developing energy efficiency and renewable energy projects that contribute to public sector decarbonisation and national energy targets. The WGES is delivered by the Carbon Trust, Energy Saving Trust and Local Partnerships (the “Delivery Partners”). This report (the “Report”) has been produced by the Delivery Partners and, whilst the views expressed in it are given in good faith based on information available at the date of this Report:- (i) these views do not necessarily reflect the views of the Welsh Government, which accepts no liability for any statement or opinion expressed in the Report; (ii) the Report is intended to provide general guidance only, rather than financial, legal or technical advice for the purposes of any particular project or other matter, and no-one in receipt of the Report should place any reliance on it in substitution for obtaining their own advice from an appropriate third party advisor; and (iii) any person in receipt of this Report should therefore obtain their own financial, legal, technical and/or other relevant professional advice insofar as they require specific guidance on what action (if any) to take, or refrain from taking, in respect of any project, initiative, proposal, involvement with any partnership or other matter to which information contained in the Report may be relevant; and (iv) the Delivery Partners accept no liability in respect of the Report, or for any statement in the Report and/or any error or omission relating to the Report.report.

## Assumptions
Organisation: | Site Name:
University of Wales Trinity St David | Dynevor Building (Swansea) |  | Floor area (m2):
6437
Site Address including postcode:
Dynevor Building, De-La Beche Street, Swansea, SA1 3EU
Date of Audit | 2025-07-09
Name of Auditor | Sean Jardine
Tool set up by: | Adam Banks |  | The costs and assumptions below are for guidance and may be superseded in the calculations.:
Carbon emission factors (kgCO2e/kWh) | Year | 2024 | Heating efficiency of boiler: | 85%
Solar PV Assumptions:
Electricity | 0.22535
Natural Gas | 0.1829 | primary fuel | £ capex per kWp | 1450
Gas-Oil/Diesel | 0.25649 | secondary fuel (1) | £ annual service cost per kWp | 20
Other Secondary Fuel |  | secondary fuel (2) | £ battery capex per kWh | 600
Other Secondary Fuel
Utility tariffs (£/kWh)
Electricity | 0.20616
Natural Gas | 0.03673 | primary fuel
Gas-Oil/Diesel |  | secondary fuel (1)
Other Secondary Fuel |  | secondary fuel (2) | Insulation Assumptions:
Other Secondary Fuel
Mixed |  |  |  | £ per m2
|  |  | Cavity wall insulation | 45
If multiple electricity tariffs, use blended tariff: |  |  | Internal wall insulation | 250
|  |  | External wall insulation | 250
| kWh | p/kWh | Loft insulation (rockwool) | 30
Day tariff |  |  | Loft insulation (sheep wool) | 60
Night tariff |  |  | Encapsulated pads above ceiling tiles | 50
Blended tariff | 0
Site Electrical Capacity:
RHI tariffs (£/kWh)
|  |  | Electrical capacity (kVA) | 400
| Tariff 1 | Tariff 2 | Max kW Demand (from HH data) | 192.4
Biomass | 0 | 0
Solar Thermal (<200 kWth) | 0
Air Source Heat Pumps | 0
Average HH Demand Profile (kW) - based on data 01/04/24 to 31/03/25:
FiT tariffs and equivalent replacement (£/kWh)
Wind or Hydro
PV generation | 0
PV export | 0.1
Inflation rates & discount rates | updated Mar 2024
Base Inflation Rate | 3.5%
Capital Costs | 3.5%
Income | 3.5%
Operating & Maintenance Costs | 3.5%
Staff Costs | 3.5%
Utilities | 10%
Renewable Tariffs | 3.5%
Real discount rate | 3.5%
Nominal discount rate | 7%
Note on C73: per current Green Book value

## Site Details
External Site Description:
The Dynevor Building is located in central Swansea and is used as the Art, Design and Media campus. The main two wings of the current building were originally constructed in 1883 as a separate Girls and Boys School, which has since been adjoined together with a link building of post 1990s construction. The original buildings have also had a number of renovations, with new roofs and double glazing installed retrospectively. The entire building consists of a 7 storey block with additional single storey ceramics building. The building predominantly consists of lecture theatres, offices, classrooms workshops and studios, with additional cafe present. The building fabric is generally in good condition with double glazing installed throughout. A plantroom for the wet heating system is located on the eighth floor. The building is heated through a mixture of radiators and air conditioning units that are installed on the roof space.
Building / Site Fabric: | Main building Block | Ceramics Building
Walls - | Solid Stone | Block construction
Roof - | Consists of pitched slate, corrugated sheet metal and flat bitumen roof areas. | Sheet metal
Floor - | Concrete | Concrete
Windows - | Double Glazed | Double Glazed
Doors - | Double Glazed glass and wood. | Double Glazed
Lighting:
Internal - | Predominantly fluorescent tube, with some LED fixtures present.
Internal Control - | Majority Manual switch
BMS: | Yes
Honeywell/Datherm
LTHW Heating: | Main building | Ceramics Building
Boilers - | 2 x 350kW Hoval Ultra Gas AMC 350 gas fired boilers | 1 x 24.5kW Vaillant ecoTEC pro 28 gas fired boiler
DHW Heating:
Water Heater - | Main building 1 x Lochinvar 44kW gas fired water heater.
Electric point of use water heaters | There were a number of electric point of use water heaters installed in specialist areas.
Heat Distribution System:
Secondary Pumps - | Grundfos
Radiator Types - | A mixture of rad types including T22, T21, T11, T10 and Ceiling Radiant Panels present.
Single / Twin Pipe - | Twin pipe system
Zones - | Radiator heating is zoned in 4 No. sections, North, East, West & Link Blocks.
Air Handling: | 4 No. AHU's that supply various areas across the building.
AHU Café/Library
AHU Lecture Theatre
AHU SonySuite
AHU Offices
Air Conditioning: | There are a number (circa 13) of A/C units that supply various areas of the building with heating/cooling.
Renewable System(s): | An extensive solar PV array has been installed at Dynevor covering the majority of available roof space. This was installed circa 2023, and has subsequently had issues with operation due to cable sizing issues. It is due to become operational in 2025.
Air Conditioning Item List
Plant Room | Toshiba A/C split with DX coil (Dantherm AHU - 5th & 7th Floor
Plant Room | Daikin VRV (2 x condenser piped together, 2 pipe system, heat/cool selector in plantroom
Ground Floor | ADG03
4th Floor | AD403/AC404/AC403
7th Floor Laster Room | Daikin A/C
7th Floor Server Room | AD7P1 - Mitsubishi A/C
7th Floor AD704 | Mitsubishi A/C twin split
5th floor server room | AE5P1 A/C
3rd floor Kitchen and Canteen | Toshiba A/C x 2
2nd Floor online broadcasting studio | AD205 - Fujitsu A/C
2nd Floor broadcasting studio equipment room | AD205 - Daikin A/C
2nd Floor | AC205 - Toshiba A/C
1st Floor Care Takers Office | Gamco A/C
AHU item List
Plant Room | Dantherm AHU - 5th & 7th floor (with Toshiba air conditioning cooling Coil)
Bag Filters x 4 (specials)
492 x 385 x 300 mm Bag
Plant Room | Sony Suite AHU
Bag filters x 2 - 592 x 287 x 300 mm Bag
Bag Filters x 4 592 x 592 x 300 mm Bag

## Consumption
Building/site consumption:
Month | Electricity (kWh) | Natural Gas (kWh) | Gas-Oil/Diesel (kWh) | Other Secondary Fuel (kWh) | Other Secondary Fuel (kWh) | Total Energy (kWh)
2024-04-01 | 40874.1 | 64961.811 |  |  |  | 105835.911
2024-05-01 | 38144.2 | 19363.395 |  |  |  | 57507.595
2024-06-01 | 32277.8 | 4643.854 |  |  |  | 36921.654
2024-07-01 | 28918.7 | 3570.375 |  |  |  | 32489.075
2024-08-01 | 25494.5 | 3455.776 |  |  |  | 28950.276
2024-09-01 | 32028.1 | 8215.615 |  |  |  | 40243.715
2024-10-01 | 47384.2 | 48667.879 |  |  |  | 96052.079
2024-11-01 | 47436.4 | 55440.71 |  |  |  | 102877.11
2024-12-01 | 41980.8 | 36755.52 |  |  |  | 78736.32
2025-01-01 | 48719.9 | 85488.914 |  |  |  | 134208.814
2025-02-01 | 47171.1 | 70944.9225 |  |  |  | 118116.0225
2025-03-01 | 47592.3834 | 54044.9904 |  |  |  | 101637.3738
Annual Total | 478022.1834 | 455553.7618 | 0 | 0 | 0 | 933575.9452
Data source used above: | HH Data | HH Data
HH data provided? | Yes | Yes |  |  |  |  | Gas consumption split
Meter ID (eg MPAN/MPRN) | 2199989674199 | 11361908 |  |  |  |  | Main Building | 432776.0738
[7 empty] | Ceramics Buildings | 22777.6881
Total Energy Usage
Utility | Annual Energy (kWh) | Annual Cost (£) | Annual Emissions (tCO2e) | £ / kWh | kgCO2e / kWh |  | Renewable Sources | Annual Generation kWh
Electricity | 478022.1834 | 98549.0533 | 107.7223 | 0.20616 | 0.22535
Natural Gas | 455553.7618 | 16732.4897 | 83.3208 | 0.03673 | 0.1829
Gas-Oil/Diesel | 0 | 0 | 0 | 0 | 0.25649
Other Secondary Fuel | 0 | 0 |  | 0
Other Secondary Fuel | 0 | 0 |  | 0
Total | 933575.9452 | 115281.543 | 191.0431 |  |  |  | Total | 0
Total Site Benchmark |  |  |  |  | Other Intensity Metric
Select CIBSE Guide F benchmark relevant to building type. |  |  |  |  | Enter most appropriate unit and value for the site if applicable (eg annual production)
If using other benchmarks: enter name and source in Building Type and the benchmark values in table.
Unit
CIBSE Building Type: | Lecture room, science |  |  |  | Annual Value for Site
Utility | Actual kWh/m2 | Good Practice kWh/m2 | Typical kWh/m2 |  | Utility | kWh /
Electricity | 74.2616 | 113 | 129 |  | Electricity
Natural Gas | 70.7711 | 110 | 132 |  | Natural Gas
Gas-Oil/Diesel | 0 |  |  |  | Gas-Oil/Diesel
Other Secondary Fuel | 0 |  |  |  | Other Secondary Fuel
Other Secondary Fuel | 0 |  |  |  | Other Secondary Fuel
Total | 145.0328 | 223 | 261 |  | Total | 0
Energy Use Profile
Utility | Type of Use | % of Utility | Annual Energy (kWh)
Natural Gas | Space Heating | 90% | 409998.3857
Natural Gas | DHW | 10% | 45555.3762
Electricity | Catering | 5% | 23901.1092
Electricity | Lighting | 30% | 143406.655
Electricity | Small Power | 15% | 71703.3275
Electricity | AC | 20% | 95604.4367
Electricity | AHU | 6% | 28681.331
Electricity | Other | 24% | 114725.324
Total |  |  | 933575.9452
Monthly Energy Consumption Profile
Electricity/Gas average annual half-hourly profile by day of week:
(based on year 24/06/24 to 30/06/24):

## REC ASHP (A2A) + ePOU
Description | Ceramic building A2A ASHP & ePOU
Technology Type | Air source heat pump (air-to-air)
Project Description | The Ceramics building is currently equipped with a 24.5kW gas fired boiler and three large gas-fired radiant tube heaters situated across the different rooms. In order to decarbonise the building, it would be proposed to replace the gas fired boiler and radiant tube heaters with an Air to Air Source split heat pump system. A 30kW spit air heat pump system would be proposed consisting of 2 x 15kw units, replacing 100% of the current gas consumption. The Air to Air heat pumps would be proposed to be installed against suitable external walls with internal wall mounted units supplying each room. The areas highlighted below are the proposed location of the external units.
Main Building Potential External Location of ASHP This potential Heat Pump location has been initially selected due to accessibility for installation and maintenance. In order to replace the DHW of the building it would be recommended to install 3 No. 2kW, 10 litre localised electric point of use DHW units which would provide the DHW consumption.
Costs | Capital Costs:
Additional Annual Operating Costs:
Annual Savings | Heating Fuel (kWh) |  | 22777.6881
| Electricity (kWh) |  | -6595.7086
Energy Costs:
| Direct GHG emissions (tonnes CO2e) |  | 4.166
| Indirect GHG emissions (tonnes CO2e) |  | -0.24171
| Other Cost Savings: |  | 0
| Potential RHI/ SEG Income: |  | 0
Total Cost Savings:
Simple Payback (years)
Lifetime Emissions savings | Lifetime GHG emission savings (tCO2e) |  | 78.4865
| Capex (£) per lifetime tCO2e savings |  | 0
Calculation & Assumption Table | The assumptions used for the energy savings calculation are summarised in the table below:
| Existing boiler efficiency | 90%
| Heat Requirement | 20499.9193 | kWh
| Present Fuel Usage | 22777.6881 | kWh
| % replaced by new HP | 100%
| New HP Capacity | 30 | kW
| Heat generated by new HP | 20499.9193 | kWh
| New HP efficiency | 309%
| New electricity requirement | 6595.7086 | kWh
| New electricity cost | 1359.7713
| Residual boiler fuel usage | 0 | kWh
| Residual boiler fuel cost | 0
| Present fuel cost | 836.6245
| RHI annual income | 0
Calculations & Assumptions | The Air to Air Heat Pump capacity has been modelled based on BRSIA benchmarking. The current buildings gas consumption has been apportioned by floor area. An average SCOP of 3.09 for the Air to Air Heat Pump and ePOU units has been used. This has been apportioned to account for the Air to Air 3.2 and ePOU of 1. A 95% space heating, 5% DHW usage has been assumed for the building. 100% of the building’s gas consumption is proposed to be removed. The electric point of use water heaters operational hours are based on 4 hours per day for 180 days per year, resulting in a total of 2160 hours per year for all units. It has been assumed that the existing solar PV array can provide 25% of the heat pump and ePOU's consumption. Fuel costs are 3.7p/kWh for gas and 20.6p/kWh for electricity respectively. Financial savings are calculated using these values. The Air to Air Heat Pump cost including supply and installation has been estimated at £2,812/kWth. A supply and install cost of £2,500 has been included for the ePOU units. A cost breakdown is summarised in the tables below. It is considered that no capital costs occured due to the increased grid capacity, however, standing charges are likely to increase. The increase in electricity standing charges is not financially considered, since standing charges for natural gas of a similar magnitude will be avoided.
Cost Breakdown Tables
| Equipment | CAPEX
HP Equipment
Buffer Tank
Installation
Radiators (Supply)
Radiators (Install)
HP control system
ePOU units (supply/install)
| TOTAL | 0
| Element | Cost £
Design and Engineering
Main equipment capital
Installation & commissioning
Project delivery
Contingency
ePOU units (supply/install)
| TOTAL | 0
Risks & Issues | Risk Category | RAG Rating | Commentary |  | Score | Weighting
| Data Risk | Amber | 12 months of HH gas consumption data was provided, this has been apportioned based on floor area. |  | 2 | 5%
| Electrical Capacity / DNO Risk | Amber | From assessment of likely additional electrical requirements, peak electrical consumption and electrical infrastructure, it is deemed unlikely that an electrical upgrade would be required. Early interaction with the DNO is critical to minimise the risk of project delays and additional costs for network upgrades. It's important to assess the MD and supply capacity and calculate anticipated additional kVA before discussing with the DNO. Further design work will be required before submitting a formal DNO application. |  | 2 | 20%
| Planning Risk | Green | The building is not listed, and therefore planning consent should be manageable. There is available space around the building for the installation of the external heat pump units. |  | 1 | 10%
| Performance Risk | Amber | If the heat pump doesn't meet the expected performance standards (e.g., COP - Coefficient of Performance) due to factors like incorrect system design, the heat pump could fall short of its intended role in improving energy efficiency and comfort. |  | 2 | 20%
| Installation Risk | Red | There is suitable space around the building for the installation of the external heat pump units. The installation of the internal wall hung units and the refrigeration pipework, would be disruptive to the usage of the building. |  | 3 | 15%
| Projected Savings Risk | Amber | It is important to set up the heating strategy correctly and to not alter this back to the previous heat strategy as it will likely affect output, efficiency of the heat pump and the resultant energy savings. |  | 2 | 5%
| Financial Risk | Red | No site specific financial risks identified, although market costs may fluctuate. |  | 3 | 10%
| Disruption Risk | Red | The installation of the internal wall hung cassettes and new internal refrigeration pipework would be disruptive to the buildings use. |  | 3 | 15%
Implementation of Energy Savings Opportunities
|  |  |  | weighted | 2.3
76.67%
Note on D60: Select from the dropdown list