## Summary Sheet
Cumulative Service Rates (per Annum)
This matrix will self populate, based on indicative service regime detailed within the Maintenance specification and the rates per unit calculated on the Service rates sheet. The Employer reserves the right to increase/reduce the number of visits, subject to review.
Equipment Type | Price per Annum (excl. VAT)
Fully Comprehensive
Passenger Lifts (upto 3 floors) | 0
Passenger Lifts (over 3 floors) | 0
Stair Lifts | 0
Platform Lifts | 0
Sub Total (per Annum) | 0
Name of Tendering Company
Name of Tenderer
Position (Director required)
Date

## Service Rates
Service Rates (per Visit)
Please provide costs in the cells provided for individual service visit
Equipment Type | Price per Visit (excl. VAT)
Fully Comprehensive
Passenger Lifts (upto 3 floors) | 0
Passenger Lifts (over 3 floors) | 0
EVAC/FF Passenger Lifts | 0
Platform Lifts | 0
Service Rates (per Annum)
This matrix will self populate, based on indicative service regime detailed within the Maintenance specification. The Employer reserves the right to increase/reduce the number of visits, subject to review.
Equipment Type | Price per Annum (excl. VAT)
Fully Comprehensive
Passenger Lifts (upto 3 floors/ 6 visits) | 0
Passenger Lifts (over 3 floors/ 10 visits) | 0
EVAC/FF Passenger Lifts | 0
Platform Lifts ( 4 visits) | 0

## Hourly Rates
Hourly Rates
Price per hour (excl. VAT)
Hourly rate for two-man operation to carry out breakdown, repair work and call-outs
Monday - Friday (Normal Working Hours)
Monday - Friday (Outside Normal Working Hours)
Saturdays
Sundays
Bank Holidays
Hourly rate for one man with shared/flexible manning to carry out breakdown, repair work and call-outs
Monday - Friday (Normal Working Hours)
Monday - Friday (Outside Normal Working Hours)
Saturdays
Sundays
Bank Holidays
Contractor to note, where travelling to and from site is involved, this shall be included within the above rates.
On-Costs
Description | Mark Up (%)
Contractor’s percentage addition on material for repair work outside of pre-tendered pricing schedules
Contractor’s percentage addition to vendors or sub-contractor’s invoices, when applicable (sub contract works by prior agreement)
Discount for payment within 30 days

## Supplementary Tests
Supplementary Tests
| Item | Price (Excl VAT)
SAFED Tests
A1 | Earth continuity
A2 | Electric safety devices | Included
A3 | Terminal speed reduction systems
A4 | Landing door interlocks | Included
A5 | Lift Machine - Investigatory test (Type A)
A6 | Lift Machine - Comprehensive test (Type B)
A7 | Overspeed governors
A8 | Governor oerated safety gear instantaneous type
A9 | Governor oerated safety gear progressive type
A10 | Safety gear orpeted by other means
A11 | Device to prevent overspeed of the ascending lift car
A12 | Unintended car movement protection
A13 | Energy dissipation buffers
A14 | Suspension system
A15 | Car overload detection warning devices | Included
A16 | Hydraulic system
A17 | Hydraulic cylinders in boreholes or similar locations
A18 | Hydraulic rupture/restrictor valves
A19 | Electrical anti-creep device | Included
A20 | Mechanical anti-creep device (Pawl or clamping device)
A21 | Low pressure detection devices (Switch or valve) | Included
A22 | Traction, brake and levelling
A23 | Car/counterweight balance
A24 | Automatic power operated doors | Included
A25 | Other supplementary tests
Additional Tests
D | Annex D annual supplementary test under BS9999/BSEN81-72

## Attendances
Attendances
| Item | Price (excl. VAT)
1 | Provide attendance for removal/refitting of shield wall panels on Platform lift for LOLER (max. 2 hours)
2 | Provide attendance for assistance during LOLER (max. 2 hours)
3 | Provide access for testing/replacement/installation of Smoke detector in lift shaft ( max. 3 hours)
4 | Provide access for water removal from Lift pit (max. 3 hours)
5 | Joint attendance for phone line issues (max. 2 hours)
6 | Retrieval of keys (during normal working hours)
7 | Lift working on arrival/ No intermittent fault (during normal working hours)

## BS & HS
BS & HS Items
| Item | Price (Excl VAT) | Comments
A | LIFT MACHINE ROOM/MACHINERY SPACE
1 | Provide fall protection (hoops) to machinery access ladder over 3m
2 | Install perimeter guard rails to machinery access trap
3 | Provide counterbalance to existing machinery access trap
4 | Install a trap Door notice (Danger of falling reclose trap door)
5 | Verifiy & mark SWL on machinery access trap
6 | Modify the machine room door such that this is lockable, openable from inside without a key and opens outwards.
7 | Install a current danger notice to the lift machine room door.
8 | Reposition the machine room light switch adjacent to the access.
9 | Install emergency lighting at the access and hand winding/lowering positions for emergency hand lowering/winding.
10 | Install a test switch for the emergency lighting
11 | Provide low headroom notice in machinery space where the lift machine room is affected by head hazards (e.g. Lifting beams) and/or less than 1.8 M in internal Height.
12 | Provide edge protection to lifting beams/ projections in machine room including black and yellow markings
13 | Modify the machine room lighting to ensure a minimum illumination level of 200 lux throughout at floor level.
14 | Install protective guards to the machine room light fittings.
15 | Install an RCD protected 13-amp electrical socket outlet in the machine room.
16 | Replace oil filled electrical circuit breaker (Ellison or similar) within a modern fused and lockable isolator (HSE Doc. HSE483/27).
17 | Replace main electrical isolator switch with lockable design in the off position.
For hydraulic lift provide a notice advising that “Lift should not be isolated for long periods unless the lift is located at the lowest level”.
18 | Install suitable guards to the tubular heaters.
19 | Suitably mark with black and yellow markings tripping hazards (e.g. trunking)
20 | Screen foreign apparatus in machine room (access routes, water tanks, ducts, etc.) Maiximum 3m x 3m
21 | Provide guard rails and steps complete with mid-rails, toe-boards & safety chain at entry point to raised machine room plinth in excess of 0.5 M.
22 | Provide adequate guarding to floor selectors. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
23 | Provide adequate guarding to governor. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
24 | Provide adequate guarding to machine/ sheaves/fixed hand-winding wheel. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
25 | Provide adequate guarding to ropes. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
26 | Provide adequate guarding to dead end hitches.
27 | Provide rope jump guards to sheave where required.
28 | Paint traction sheaves, rope diverters and hand-winding wheels safety yellow
29 | Provide hand-winding wheel (smooth rimmed).
30 | Provide brake release lever (or manual lowering device – HYD)
31 | Provide hand winding/lowering car position indication unit
32 | Provide brake with two separate springs and mountings in accordance with EN81-20.
33 | Provide a shut off valve in the motor room between the hydraulic Jack and tank unit.
34 | Provide a hand pump and pressure gauge on hydraulic lifts.
35 | Provide an anti-creep system on hydraulic lift.
36 | Provide a low-pressure device on hydraulic lift.
37 | Display hand winding/lowering instructions adjacent to lift machine/tank.
38 | Provide a safety push to stop switch adjacent to machine.
39 | Identify and mark the main switches, controllers, machines, selectors, governors & associated equipment.
Where more than one lift is installed identify the top and bottom landings.
40 | Provide notices warning of interconnecting wiring. (Duplex or group).
41 | Provide notice on controller warning of live terminals; isolate before opening.
42 | Provide marking and notices to group/signal supplies.
43 | Provide 700 mm clear space to front/rear the lift controller.
44 | Install lifting beams (5m)
45 | Test and mark lifting beams with the SWL.
46 | Install machinery access trap for machinery repairs.
47 | Install electric shock notice adjacent to the main electrical isolator switch.
48 | Provide lift electrical circuit wiring diagrams.
49 | Provide fire extinguisher.
50 | Install 50 mm high ferrules around all openings through machine floor slab.
51 | Provide means to contain oil spill on hydraulic lift (bund) (Oil Storage Regulations 2001).
52 | Install lift controller covers and doors.
53 | Install guards & warnings to exposed 230 & 400-volt terminals in the control panel.
54 | Provide electrical isolation safety mats front and rear of controller panels.
55 | Provide an overspeed governor to operate the safety gear.
56 | Install an electrical overspeed trip switch to the overspeed governor.
57 | Provide means to detect machine room temperature.
58 | Provide Engineers tool board
B | PULLEY ROOM
59 | Provide push to stop switch adjacent to pulley room door.
60 | Paint pulleys safety yellow.
61 | Provide adequate guarding to all overhead pulleys. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
62 | Provide adequate guarding to overspeed governor.
63 | Provide adequate guarding to ropes. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
64 | Provide adequate guarding to dead end hitches.
65 | Install 50 mm high ferrules around all openings through machine floor slab.
66 | Provide pulley room lighting to provide a minimum level of illumination 200 lux throughout at floor level.
67 | Provide pulley room emergency lighting.
68 | Provide light switch adjacent to pulley room access.
69 | Provide guards to pulley room light fittings.
70 | Provide 13-amp electrical socket outlet in pulley room.
71 | Provide imperforate pulley room floor.
C | LIFT CAR TOP
72 | Install 100 mm high toe-board around the perimeter of the lift car top.
73 | Provide car top balustrade, mid rail, toe board & notice. Handrail to be at least 100 mm from any equipment.
74 | Screen any excessive gaps between the car top and Lift shaft walls, with all ledges within the shaft in excess of 200 mm to be ramped off.
75 | Provide a tested anchorage at the scenic lift car top for Safety Harness, to be marked with SWL ‘90kg’.
76 | Provide ‘Danger of Falling notice advising that fall arrest equipment must be worn at lift car top.
77 | Provide lift car top communication system by way of engineer’s alarm or voice communication.
78 | Provide top of car inspection control, incorporating light and socket outlet, and mounted vertically, and operable within 1 M of the entrance & within 0.3 M of a refuge space (where applicable).
79 | Install a stop/run switch within 1 M of the entry point for maintenance personnel.
80 | Provide lift car top light.
81 | Provide lift car top emergency lighting minimum 5 lux for 1-hour.
82 | Install maintenance test limit which will stop the ascending lift when on maintenance control such that minimum escape provisions are assured at the terminal floors.
83 | Provide restricted headroom notice where top safety clearance is insufficient in terms of EN81-20.
84 | Identify the safety refuge space at the car top.
85 | Modify the lift car top such as to support anticipated personnel (minimum 2) plus tools.
86 | Provide lift car top rope pulley guards. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
87 | Provide guard to counterweight rope pulley or ram head pulley on hydraulic lift. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
88 | Provide "Anti-Surf" device on Car top
89 | Provide a “Do Not Ride on Car Top” notice in cases in which no lift car safety gear or hydraulic rupture valve is installed.
D | LIFT CAR
90 | Provide a suitable communication system between the lift car and motor room in the case of lift car travel in excess of 30 M.
91 | Install a lift car door/gate.
92 | Install an imperforate car door/gate. (Note: Mid-bar gate designs to have an emergency stop switch in the lift car adjacent to the gate).
93 | Provide lift car door lock and interlock during travel.
94 | Provide lift car interior load plate in lift car with SWL, manufacturer’s name and reference No.
95 | Provide non-contact lift car door detector to detect obstacles 50 mm in diameter in a vertical distance between 25 mm above the sill to 1. M above the sill.
96 | Provide a means of opening the car door which is exterior to the car at low and high level to permit rescue from 1.2 M above and below the landing.
97 | Provide lift car alarm bell and maintained supply.
98 | Provide replacement Car light to BSEN81-20
99 | Provide lift car interior emergency lighting (3 hours)
100 | Provide a safety apron on the lift car platform minimum 750mm deep. Design to withstand EN81-20 300 N test force.
101 | Provide safety gear which is released automatically by raising of the lift car.
E | LIFT WELL & PIT
102 | Provide lift shaft smoke ventilation to local Building Regs requirements.
103 | Provide rupture valve on hydraulic jack of hydraulic lift cars not equipped overspeed governor operated safety gear.
104 | Provide slack rope/chain device.
105 | Test and mark lifting beam in lift shaft of hydraulic lift.
106 | Provide lifting beam/facilities in Lift shaft.
107 | Provide safety retaining system to overhead pulleys located directly above the lift car.
108 | Provide Lift shaft lighting (500 mm from top & bottom & interspaced) to give minimum 50 lux 1 M above car top & 1 M above pit floor to EN81-20, including Emergency at top & bottom of lift well UPTO 6 FLOORS
109 | Lift Shaft lighting per additional floor
110 | Install lift shaft pit emergency lighting.
111 | Install two-way switching, from the lift machine room and lift pit, to the lift shaft lighting. Pit switch to be within 0.75 M horizontally from door frame inner edge & not less than 1 M above the sill level.
112 | Provide suitable protective covers/guards to Lift shaft lights.
113 | Provide imperforate landing doors.
114 | Provide doors with flush internal faces.
115 | Install landing door closers.
116 | Provide EN81-20 landing door emergency interlock release at all floors.
117 | Install a door release which is operable from the lift pit floor or pit ladder & which is within 0.8 M horizontally of the pit ladder in accordance with EN81-20.
118 | Install an EN81-20 engineer’s pit inspection control device complete with external reset device at lower landing. Device to be located within 0.3 M of a refuge space.
119 | Provide landing door slave contacts or mechanical connection.
120 | Provide pre-locking and retiring cam to manually operated gates on goods lifts.
121 | Provide covers to interlocks which are easily removed for inspection.
122 | Provide electrical warning notices to all switches where circuits are above 50 Volts.
123 | Provide fascia covers or toe guards to landings where required. Design to withstand EN81-20 300 N test force.
124 | Provide EN81-20 counterweight screen extending 2 M vertically above the top of compressed buffer such that the buffers & buffer switches are accessible & protecting side areas where these are in excess of 300 mm in depth. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857.
125 | Provide counterweight screen with permanent sign designating minimum and maximum counterweight/buffer clearances.
126 | Provide division screens full height of Lift shaft. Design to withstand EN81-20 1000 N test force. Guarding design to EN81-20 BS EN ISO14120 & BS EN ISO13857. UPTO 6 FLOORS
127 | Provide a division screen (per additional floor)
128 | Provide a EN81-20 compliant lift pit ladder.
129 | Provide a pit switch of push to stop design, positioned not less than 0.4 above the sill and not more than 2 M above pit floor, & within 0.75 M of the door frame inner edge (Pits up to 1.6 M deep).
130 | Provide two pit stop switches one positioned not more than 1.2 M above pit floor & accessible from a refuge space & the other not more than 1 M above the sill & within 0.75 M of the door frame inner edge (Pits in excess of 1.6 M deep).
131 | Supply landing door barrier to BS 7255.
132 | Provide emergency release key.
133 | Supply and install electrically interlocked pit props or guide clamps for lifts with restricted pit depth.
134 | Provide a notice – “position prop or clamps before entering”.
135 | Provide reduced pit depth notice.
136 | Identify the safety refuge space in the lift pit & mark with signage.
137 | Install an RCD protected 13-amp electrical socket outlet in the lift pit.
138 | Provide guard to governor tension weight pulley.
139 | Provide governor tension weight switch.
140 | Provide buffers in the pit to replace solid timber blocks.
141 | Provide buffer check switches to hydraulic buffers.
142 | Provide lift pit communication system by way of engineer’s alarm or voice communication.
143 | Install counterweight safety gear in cases in which there is an accessible area/void in the area directly below the lift pit.
144 | Paint the lift counterweight safety yellow.
F | AUTODIALLER
Passenger Lifts
145 | Install BSEN81-28 compliant Autodialler
146 | Replace existing closed protocol Autodialler, including provisions for BSEN81-28 compliance
147 | Provide a GSM unit for Autodialler
148 | Provide 12 month Unlimited Sim for GSM unit
Platform Lifts
149 | Install BSEN81-28 compliant Autodialler
150 | Replace existing closed protocol Autodialler, including provisions for BSEN81-28 compliance
151 | Provide a GSM unit for Autodialler
152 | Provide 12 month Unlimited Sim for GSM unit

## Asset List
| Postcode | Type | Number of Floors | Rated Load | Manufacturer | Year
Maes Trisant (Lift 2) | CF72 8RQ | HPL | 3 | 1000Kgs | E.A Foulds | 1981
Ty Bethania | CF42 6AX | HPL | 4 | 630kg | Otis | 1990
Martyrs Reach | SA2 0BZ | HPL | 4 | 630kg | Otis | 1999
18 Swn Y Nant, Blaengwinfi, | SA13 3UR | VPL | 2 | 25Okg | Terry Lifts | 2004
Lord Nelson House | SA1 1NE | HPL | 4 | 630kg | Otis | 2000
Ty Mawr | SA1 6AZ | HPL | 4 | 630kg | Otis | 2000
Henllys & Wind St Office (NW6825) | SA1 1DP | HPL | 5 | 630kg | Otis | 2000
Henllys & Wind St Office (NW6826) | SA1 1DP | HPL | 6 | 630kg | Otis | 2000
Henllys & Wind St Office (NW6827) | SA1 1DP | HPL | 7 | 630kg | Otis | 2000
Mermaids Retreat | SA3 4EE | HPL | 4 | 630kg | Express Evans | 2001
Runnymeade Flats | SA2 0QF | HPL | 5 | 630kg | Kone | 2006 (MOD)
Capstan House | SA1 3UL | TMRL | 5 | 630kg | Otis | 2004
Tower Court | SA1 6QB | HPL | 2 | 450kg | Kone | 2014 (MOD)
Trinity Court | SA1 5DW | HPL | 6 | 630kg | Kone | 2014 (MOD)
Clos Coed Nant | SA1 2LU | HPL | 3 | 630KG | Kone | 2014 (MOD)
Cwrt May | SA11 1NG | HPL | 3 | 630kg | Kone | 2014 (MOD)
Llys Nazareth | CF41 7BS | HPL | 4 | 630kg | Express | 1950
Ysbryd Y Mor | SA12 7PB | HPL | 3 | 1250kg | CLC/Orona | 2005
17 Goytre Close Port Talbot | SA13 2YL | VPL | 2 | 250kg | Terry Lifts | 2010
Constantine Court | CF40 1QL | VPL | 3 | 630kg | Otis | 2010 (MOD)
Llys Yr Onnen | CF45 3TS | HPL | 3 | 630kg | Thyssen | 2010 (MOD)
Caswell Hall | SA1 6JP | TMRL | 4 | 630kg | Otis | 2006
Ty Victoria (700) | SA11 1EF | TMRL | 4 | 630kg | Otis | 2006
Ty Victoria (701) | SA11 1EF | TMRL | 4 | 630kg | Otis | 2006
Orchard Court | SA1 5EJ | HPL | 4 | 630kg | Stannah | 2011 (MOD)
Orchard Court | SA1 5EJ | HPL | 4 | 630kg | Stannah | 2011 (MOD)
Barons Court | SA1 5BH | VPL | 3 | 410kg | Aritco/Gartec | 2011
Maddison House | SA1 5AW | TMRL | 7 | 450kg | Otis | 2007
Porth Nedd | SA11 1BL | TMRL | 4 | 630kg | Otis | 2007
Harlequin Court | SA11 1LZ | HPL | 5 | 630kg | Otis | 2008
Harlequin Court | SA11 1LZ | HPL | 5 | 630kg | Otis | 2008
Mariners Court (5369) | SA1 8QS | TMRL | 7 | 630kg | Otis | 2008
Mariners Court (5370) | SA1 8QS | TMRL | 6 | 630kg | Otis | 2008
Mariners Court (5371) | SA1 8QS | TMRL | 4 | 630kg | Otis | 2008
Ty Heledd | SA1 4AG | TMRL | 6 | 630kg | Otis | 2008
Beacon Cymru, 9 Compton Road, | CF40 1BE | TMRL | 5 | 630kgs | Orona | 2008
Compton Court | CF40 1BE | TMRL | 2 | 630kgs | Orona | 2008
Twyn Teg (7417) | SA10 7RN | TMRL | 5 | 1000kg | Otis | 2009
Twyn Teg (7418) | SA10 7RN | TMRL | 3 | 1000kg | Otis | 2009
Twyn Teg (7419) | SA10 7RN | TMRL | 3 | 1000kg | Otis | 2009
Flats 1-35 Ty Ddewi | CF41 7BG | HPL | 3 | 630kgs | Otis | 1964
Llys Ben Bowen Thomas | CF41 7SB | HPL | 3 | 630kgs | Unknown | 1980
Ysbryd Y Mor Platform Lift | SA12 7PB | VPL | 3 | 410kg | Gartec | 2015
Jubilee House Aberavon | SA12 6QL | TMRL | 4 | 630kg | Otis | 2010
Castle Lane, Castle Quarter - Platform | SA1 2AF | VPL | 2 | 410kg | Gartec | 2015
Maes Trisant (Lift 1) | CF72 8RQ | HPL | 3 | 1000kg | Triangle Lift Services | 1981
Penderyn Hse | SA13 1NR | TMRL | 4 | 630kg | Otis | 2011
Barons Court | SA1 5BH | TMRL | 6 | 630kg | Otis (Evac) | 2011
Harbour Quay | SA1 8QZ | TMRL | 6 | 630kg | Otis | 2011
Harbour Quay | SA1 8QZ | TMRL | 6 | 630kg | Otis | 2011
Urban Village Warehouse | SA1 1NW | VPL | 3 | 410kg | Gartec | 2016
26 Alexander Road, Swansea, SA4 4MN | SA4 4MN | VPL | 2 | 410kg | Aritco | 2017
Coastal Housing Head Office | SA1 1NW | TMRL | 5 | 630kg | Otis | 2013
Coastal Housing Head Office | SA1 1NW | TMRL | 5 | 630kg | Otis | 2013
Strand Court Lift 1 | SA1 1NW | TMRL | 13 | 1275kg | Otis (FFL) | 2013
Strand Court Lift 2 | SA1 1NW | TMRL | 13 | 1000kg | Otis | 2013
Urban Village Mews | SA1 1NW | TMRL | 6 | 630kg | Otis | 2013
Customs House | SA13 1HG | TMRL | 5 | 630kg | Kone | 2013
Customs House | SA13 1HG | TMRL | 5 | 630kg | Kone | 2013
Bethesda Court (1-8) | SA1 2EY | TMRL | 4 | 440kg | Stannah | 2014
Bethesda Court (9-16) | SA1 2EY | TMRL | 4 | 450kg | Stannah | 2014
Bethesda Court (17-35) | SA1 2EY | TMRL | 4 | 450kg | Stannah | 2014
Bethesda Court (36-43) | SA1 2EY | TMRL | 4 | 450kg | Stannah | 2014
Castle Lane, Castle Quarter Passenger | SA1 2AF | TMRL | 7 | 1000kg | Kone | 2015
Castle Lane, Castle Quarter - Goods | SA1 2AF | TMRL | 2 | 1600kg | Kone | 2015
Paradise View | SA1 6PU | TMRL | 3 | 630kg | Kone | 2016
Paradise View | SA1 6PU | TMRL | 3 | 630kg | Kone | 2016
Urban Village Creative Cluster | SA1 | TMRL | 5 | 630kg | Kone | 2016
Strand Quarter Lift 1 43064154 | SA1 | TMRL | 4 | 630kg | Kone | 2017
Leonard Charles, Swansea | SA1 3HT | TMRL | 5 | 630kg | CLC/Orona | 2017
Strand Quarter Lift 2 | SA1 | TMRL | 7 | 630KG | Kone (FFL) | 2018
Cwrt Y Afon, Bridgend | CF31 1DP | TMRL | 5 | 630KG | Kleemans | 2018
Argyle Court | SA1 4AZ | TMRL | 4 | 630kg | Kleeman | 2020
Osbourne Street 34-37 | SA1 3UL | TMRL | 3 | 630kg | Kone | 2020
Mackworth Court Block 1 | SA1 5AA | TMRL | 5 | 630Kkg | Kone | 2021
Mackworth Court Block 2 | SA1 5AA | TMRL | 4 | 630kg | Kone | 2021